Revision of the technical specifications C10/21 – Mains decoupling relays and C10/23 - Multifunction IED relays and corresponding amendment to technical prescription C10/11

Following the publication of the latest version of the technical prescription C10/11 (edition 2.1 of 01/09/2020) applicable for power-generating plants, the technical specifications C10/21 for interface protection relay or mains decoupling relay and C10/23 for multifunction IED relay need to be aligned. This opportunity has been used to combine the two technical specifications in a single document and to align the layout with other technical specifications.

Although a power-generating plant is often only a tiny part of the electrical grid, the ever increasing number of them might have a significant impact on the stability of the grid when unexpected circumstances take place. One of the protection systems present is the so-called Loss of Mains protection checking if the power-generating plant is still connected to the network. The technical specification C10/11 currently allows the choice between three island detection methods. To strive for a better balance between system stability and detection/safety, the requirements of the island detection method need to evolve. Safety is and remains a top priority during these events. Based on growing experiences the ‘Vector jump’ as one of the methods is abandoned as it is more susceptible to inadvertent operation during non-islanding faults. Multi-criteria methods like ‘Activation of a narrow frequency window based on local voltage criteria’ as clearly described in European standardization are more resilient and become the preferred methods. This is reflected in the new technical specification as both the ‘Rate of Change of Frequency’ (RoCoF) and the ‘Activation of a narrow frequency window based on local voltage criteria’ are the imposed island detection functions in the Loss of Mains protection. This change in requirement compared to the technical prescription C10/11 has been agreed between the DSO’s and the TSO Elia and will also be submitted to the three regional regulators for approval. A transition period till October 1, 2021 is planned for this change in requirement at which moment the old C10/21 and C10/23 lists of homologated relays are no longer valid. Please be aware that the new homologation process will take time (min. 6 to 8 weeks depending on the number of applications).

The additional expectations beside the technical requirements are explicitly included in the technical specification as well as the list of functional tests which will be performed as part of the homologation process.

Modalities of this consultation

Synergrid has drafted a revision of the technical specifications C10/21 – Mains decoupling relays and C10/23 - Multifunction IED relays. Due to the change in requirement compared to the technical prescription C10/11 a corresponding amendment to the technical prescription C10/11 has also been drafted.

- This consultation runs from today up to and including August 23, 2020. Any interested person can participate by sending their comments to the email address consult@synergrid.be at the latest on August 23, 2020.
- For the introduction of the comments, we expressly ask you to use the response form in excel “COMMENT SHEET” published hereunder. Only comments entered using this form will be taken into consideration.

Documents:
You will find hereunder the full documentation (mainly available in EN):
- Comment sheet

- Technical specification C10/21 and C10/23 version 2.1

- Amendment to technical prescription C10/11:

NL:

FR:

EN:

Results
Synergrid has received only comments from one stakeholder. These can be found in the compilation document:

After evaluation within Synergrid, only minor modifications were made without changing the technical contents of both documents. Consequently the amendment to the technical prescription C10/11 has been sent for approval to the regional regulators.