## 1 GLV
GLVxxx-yy |  | (brand name) | (series name)
C10/26 - DECLARATION OF CONFORMITY for power-generating units GLV ed2.1.4 (10/2025)
for compliance with annex D "Technical basic requirements regarding the power-generation units"of the Synergrid prescription C10/11 ed2.4 (15/10/2025).
The undersigned, |  | Manufacturer: |  | Represented by:
|  | Address: |  | Country:
email:
|  | Country: |  | Telephone:
Hereby declares that each production unit completed in the list in tab 2 'list of power-generating units' of this homologation application complies with the following conditions:
1. The power-generating unit complies with the relevant requirements set out in annex D "Technical basic requirements regarding the power-generation units" of the Synergrid prescription C10/11 ed2.4 (15/10/2025).
2. In order to substantiate this, a technical file has been submitted for each product series of the 'C10/26 list of power-generating units' of this homologation application. Each technical file shall be drawn up on the basis of a checklist Annex D, duly and correctly completed by the manufacturer, accompanied by all the required proof of conformity.
2.1 For technical requirements for which the required proof of conformity (column J in checklist annex D) is a declaration of honour by the manufacturer, no additional documents are needed. By signing and dating this declaration of conformity, the manufacturer declares the correctness of the information (compliant / non-compliant / not applicable) provided by him or her in columns K, L and M of this checklist.
2.2. For technical requirements for which the required proof of conformity (column J in checklist Annex D) is a test report or a certificate, the necessary test reports and/or certificates are available in the technical file:
- Certificates have been issued by an EN 45011 (or ISO 17065:2012) certification body accredited for these materials.
- Test reports have been established by an ISO 17025:2005 or ISO 17065:2012 laboratory accredited for these tests.
Homologated by Synergrid on:
Manufacturer's signature: |  | Digitally signed, see last page |  | Synergrid signature: | Digitally signed, see last page

## 2 list power-generating units
POWER-GENERATING UNITS TO BE HOMOLOGATED FOR THE LIST C10/26 ACCORDING TO THE REQUIREMENTS OF ANNEX D OF THE TECHNICAL PRESCRIPTION C10/11 ed2.4 (15/10/2025)
2. C10/26 list with power-generating units in accordance with annex D of C10/11 ed2.4 (15/10/2025)
GLVxxx-yy
checklist ed2.1.4 (10/2025)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | [5 empty] | 12 |  |  |  | 13 | [5 empty] | 14 | 15
SYNERGRID reference number (GLVxxx-yy-zzzz) | BRAND NAME | Name of the product SERIES | REFERENCE of the model / type of the unit | FIRMWARE VERSION | ONLY for units (suitable for) energy storage: Name and reference of the power control system |  | POWER |  | 1-phase or 3-phase | ADDITIONAL CHARACTERISTICS | [5 empty] | LIMITATIONS |  |  |  | APPLICATION
[7 empty] | Pac,r rated (active) power (W) | Smax maximum apparent power (VA) |  | D.3 | (...) | D.4.1 | D.6.2 | D.7.2 | () | D.7.1 | D.4.3 | D.9.1 | (...) | [6 empty] | Additional information | Synergrid homologation approval date
[5 empty] | Only for “Small” storage PGU’s : Power control system type EnFluRi (name), and/or use of P1 port of smart meter of DSO (indication “P1”). | All other (bigger) storage PGU’s : Other power control system (name) |  |  |  | integrated automatic separation system | RfG type B or "RfG type B ready" = suitable for use in installation ≥ 1MW | additional operating frequency range (51,5 Hz - 52,5 Hz) | power response to underfrequency | active power reduction P(U) | compliant power control system provided (e.g. EnFluRi) | only homologated for "small power-generating installations" | only homologated for connection to HV-network | only homologated for use in module < 800W | only homologated as a backup power system according to §2.1.1 | Solar energy | Wind energy | CHP (combined heat & power) | Energy storage | Backup power system | Other
[28 empty] | 0 | 0 | 0
[28 empty] | 0 | 0 | 0
[28 empty] | 0 | 0 | 0
[28 empty] | 0 | 0 | 0
[28 empty] | 0 | 0 | 0
[28 empty] | 0 | 0 | 0
[28 empty] | 0 | 0 | 0
[28 empty] | 0 | 0 | 0
[28 empty] | 0 | 0 | 0
[28 empty] | 0 | 0 | 0
[28 empty] | 0 | 0 | 0
[28 empty] | 0 | 0 | 0
[9 empty] | 1-phase | [16 empty] | Plug&play
[9 empty] | 3-phase | [16 empty] | Suitable for V2G
Generator (gas)
Generator (hydro)
Generator (diesel)
Generator (biomass)
EXPLANATIONS FOR THE COMPLETION OF THE TABLE
Column | Title | Remarks
1 | SYNERGRID reference | In the case of a positive homologation, each C10/26-homologated power-generating unit is given a unique Synergrid reference number:
| number | xxx = unique reference or the manufacturer
| (GLVxxx-yy-zzzz) | yy = serial number of manufacturer xxx's record xxx
zzzz = unique unit reference for the manufacturer xxx
Note : "GLV" is the internal Synergrid-abbreviation for Declaration of Conformity, based on the Dutch word "Gelijkvormigheidsverklaring".
2 | Brand name | Brand name under which the unit is marketed on the Belgian market.
3 | Name of the product series | Name of the product range. Note: For each separate product range (or each group of units with common characteristics) a separate checklist according to Appendix D is required (sheet 3) together with the corresponding conformity proof documents.
4 | Reference of the model / type of the unit | Unique product name or reference. Units of the same product range must be unequivocally distinguished from each other through this name or reference.
5 | Firmware version | Reference of the firmware version of the unit.
6 | power control system type EnFluRi | This case is only applicable for units (suitable for) energy storage, provided with a power control system of type EnFluRi: Name and reference of the power control system of type EnFluRi, compliant to the requirements in C10/11 §4.1.7 and §7.11.2.1
7 | other power control system | This case is only applicable for units (suitable for) energy storage, provided with a power control system of another type than EnFluRi: Name and reference of the power control system, compliant to the requirements in C10/11 §7.11.2.2
8 | Pac,r rated (active) power (W) | Active (electrical) power in W at the terminals of the unit, as stated on the technical sheet / data sheet / brochure and nameplate. (For photovoltaic inverters: see also definition in §3.2.5 of IEC 62894 2016-11)
9 | Smax - maximum apparent power (VA) | Maximum apparent (electrical) power at the terminals of the unit, as stated on the certificate / the test report / the technical sheet / data sheet / brochure.
10 | 1-phase or 3-phase | Indicate whether the unit is single- or three-phase. This characteristic refers to the unit itself, not to the nature of the connection to the distribution network to which the unit can be connected.
11 | Additional characteristics | In these columns optional additional characteristics of the units are indicated, following the information in checklist annex D and the corresponding technical file. Put an "X" at each relevant additional characteristic. Note: Only units < 1 MW that are "type B ready" may be applied in an installation ≥ 1 MW (installation "type B" according to the European Network Code RfG). A unit < 1 MW is only "type B ready" if it complies with all optional properties ticked in column I of the checklist Annex D.
12 | Limitations | These columns specify limitations of the units to their application in certain types of installations, in accordance with the information in the checklist in annex D and the corresponding technical file. Put an "X" to each relevant limitation.
13 | Application | Indicate the applications for which the unit is suitable. Include an "X" with each application for which the unit can be used.
14 | Additional information | Additional information about the application of the unit(s): Plug&play, Suitable for V2G, Generator (gas), Generator (hydro), Generator (diesel), Generator (biomass), … .
15 | Synergrid homologation approval date | Date on which the submitted homologation file was approved by Synergrid. - An approval will be granted as soon as Synergrid has a fully compliant homologation dossier. - A homologation only remains valid under the following conditions: - No changes that have an influence on the initial approval are made to (the production of) the units. - There is no new edition of prescription C10/11, or the homologation remains valid under the most recent edition of the prescription C10/11. - The validity date of the test reports in the technical file submitted for approval has not been exceeded. See also the general Synergrid procedure S1/01 for homologation of material, which is applicable.
See also the general Synergrid procedure S1/01 for homologation of material, which is applicable.

## 3 checklist annex D
POWER-GENERATING UNITS TO BE HOMOLOGATED FOR THE LIST C10/26 ACCORDING TO THE REQUIREMENTS OF ANNEX D OF THE TECHNICAL PRESCRIPTION C10/11 ed2.4 (15/10/2025)
3. Checklist according to the requirements of Annex D of Technical Prescriptions C10/11 ed2.4 (15/10/2025)
GLV |  | (brand name) | (series name - one or more series) |  | checklist ed2.1.4 (10/2025)
Instructions for completing this checklist annex D: see at the bottom of the table.
Reference in annex D of C10/11 ed2.1 dated 01.09.2019 |  | Characteristic | Requirement - black = mandatory - blue = additional information needed in column M | Reference NC RfG | Applicable on what units? |  |  | Required proof of conformity | C10/11 Compliant? | Manufacturer’s reference of proof of conformity | Additional information | Evaluation Synergrid | Explanation Synergrid | Relevant standards for proofs of conformity indicative, non-exhaustive list
[5 empty] | General units other than backup power systems ("emergency groups") according to C10/11 definition §2.2.1 | emergency groups C10/11 §2.2.1 | Specific type B (RfG) |  | completion is considered to be a declaration of honour by manufacturer | available in the technical file: see list of proofs of conformity (sheet 4) | to be filled in by the manufacturer where required (see blue italics) or preferred |  |  | VDE-AR-N 4105: 2018-11 | DIN VDE V 0124-100: 2019-09 | Unit Certificate Req. Listed in (VDE4110:2018-11) | VDE-AR-N 4110:2018-11 | FGW TR 3 Rev 25
(n.a.) | Type of power-generating unit (main text C10/11 §4.1.6)
| Is the unit connected to the distribution network in a synchronous or non-synchronous way ? | non-synchronous units | (indicate compliant or non-applicable in column K) |  | all units
|  | synchronous units | (indicate compliant or non-applicable in column K) |  | all units
(n.a.) | ONLY for (units suitable for) energy storage systems : power control system (main text C10/11 §4.1.7 and 7.11.2)
| Is a compliant EnFluRi system provided, and/or is the use of use of the P1 port of the smart meter of the DSO possible (indication “P1”). | See C10/11 §4.1.7 and §7.11.2.1 | enter in field "Additional information": Name and reference of the provided EnFluRi system. |  | ONLY for (units suitable for) energy storage systems | [5 empty] | (give information)
|  | The EnFluRi sensor and its control system are compliant with the relevant requirements in the FNN Hinweis "Anschluss und betrieb von Speichern am Niederspan-ningsnetz" (see www.vde.com/de/fnn) | manufacturer declaration |  | ONLY for (units suitable for) energy storage systems |  |  | declaration
| Is a compliant power control system, other than an EnFluRi-system provided? | See C10/11 §7.11.2.2 | enter in field "Additional information": Name and reference of the provided power control system |  | ONLY for (units suitable for) energy storage systems | [5 empty] | (give information)
|  | The sensor and its control system are compliant with the relevant requirements in C10/11 §7.1.2.2 | manufacturer declaration |  | ONLY for (units suitable for) energy storage systems |  |  | declaration
D.3 | Integrated automatic separation system (power ≤ 30 kVA)
| Protection functions | Function | Trip setting: settings according to annex C, §C.1 of C10/11
|  | Overvoltage 10 min mean | 230 V + 10% no delay * |  | units ≤ 30kVA with internal automatic separation system | yes |  | certificate / test report | [5 empty] | 6.5.2 | 5.5.7
|  | Overvoltage | 230 V + 15% no delay * |  | units ≤ 30kVA with internal automatic separation system | yes |  | certificate / test report | [5 empty] | 6.5.2 | 5.5.7
|  | Undervoltage | 230 V - 20% no delay * |  | units ≤ 30kVA with internal automatic separation system | yes |  | certificate / test report | [5 empty] | 6.5.2 | 5.5.7
|  | Overfrequency | 51,5 Hz no delay * |  | units ≤ 30kVA with internal automatic separation system | yes |  | certificate / test report | [5 empty] | 6.5.2 | 5.5.7
|  | Underfrequency | 47,5 Hz no delay * |  | units ≤ 30kVA with internal automatic separation system | yes |  | certificate / test report | [5 empty] | 6.5.2 | 5.5.7
|  | detection of an island situation (LoM) | according to EN 62116 (in IEC/EN 62116 ed.2: see §6, annex B) Enter in field "Additional information": what LoM method according to EN 62116 and what settings |  | units ≤ 30kVA with internal automatic separation system | yes |  | certificate / test report |  |  | (give information) |  |  | 6.5.3 a) | 5.5.10
* "No delay" means that no time delay is added to the intrinsic technical duration required to initiate the disconnection. The total operate time may not exceed 200 ms.
| ‘Single Fault Tolerance’ |  | according to EN 50549-1 (2019), §4.13 |  | units ≤ 30kVA with internal automatic separation system | yes |  | certificate / test report | [5 empty] | 6.1 | 5.5.2
D.4 | Operating ranges
D.4.1 | Operating frequency range |  |  | Art 13 1
|  | Frequency domain | Duration
|  | 47,5 Hz – 49,0 Hz | 30 minutes |  | all units | no |  | declaration or certificate / test report | [7 empty] | 11.2.3.1 | 10.2.1.2 | 4.7.2
|  | 49,0 Hz – 51,0 Hz | Permanent |  | all units | no |  | declaration or certificate / test report | [7 empty] | 11.2.3.1 | 10.2.1.2 | 4.7.2
|  | 51,0 Hz – 51,5 Hz | 30 minutes |  | all units | no |  | declaration or certificate / test report | [7 empty] | 11.2.3.1 | 10.2.1.2 | 4.7.2
|  | operation within 51,5 Hz - 52,5 Hz possible? | enter in field "Additional information": yes / no |  | OPTIONAL for all units | no |  |  |  |  | (give information)
|  | maximum duration of operation in this frequency range (51,5 Hz - 52,5 Hz) | enter in field "Additional information": (duration) |  | OPTIONAL for all units | no |  |  |  |  | (give information)
D.4.2 | Maximum admissible power reduction in case of underfrequency |  |  | Art 13 4 Art 13 5
| reference ambient conditions | indicate if the capacity is affected by ambient conditions | - fill in "yes / no" in field additional information. - If "yes": also confirm the reference ambient factors at which the capacity was determined, as mentioned in D.4.2. |  | all units | no |  | declaration |  |  | (give information)
D.4.2.1 - Limit for non-synchronous power-generating technology (power park modules)
| limiting curve (see figure in D.4.2.1 and table 10) maximum allowed DP/Pmax | Parameter | Value
|  | Frequency threshold | 49 Hz |  | non-synchronous units | no |  | declaration
|  | Inclination of the limiting curve | 2%/Hz |  | non-synchronous units | no |  | declaration
D.4.2.2 - Limits for synchronous power-generating technology
| limiting curve (see figure 9 + table 11) maximum allowed DP/Pmax | Parameter | Value
| Transient domain (between t1 and t2) | Frequency threshold | 49 Hz |  | synchronous units | no |  | declaration
|  | Inclination | 2%/Hz |  | synchronous units | no |  | declaration
|  | t1 | ≤ 2 seconds |  | synchronous units | no |  | declaration
|  | t2 | 30 seconds |  | synchronous units | no |  | declaration
| Steady state domain (steady state, from t2 onwards) | Frequency threshold | 49,5 Hz |  | synchronous units | no |  | declaration
|  | Inclination | 10%/Hz |  | synchronous units | no |  | declaration
|  | t3 | ≥ 30 minutes |  | synchronous units | no |  | declaration
D.4.3 | Continuous operating voltage range
| Wide (general) operating range: suitable for connection to both LV and HV networks |  | 85% Uref < U < 110% Uref where Uref = - LV connection: Uref = Un = 230 V - HV connection: Uref = Uc = declared voltage for U < 95% Un reduction of apparent power is allowed |  | all units | yes |  | declaration
| Limited operating range: ONLY suitable for a connection to the HV network (insufficient for connection to LV network) |  | 90% Uc < U < 110% Uc where Uc = declared voltage for U < 95% Uc reduction of apparent power is allowed |  | units ONLY suitable for a connection to HV (Limited operating range) | yes |  | declaration or certificate / test report | [7 empty] | 11.2.4 | 10.2.1.1 | 4.7.2
D.5 | Immunity to disturbances ("withstand capabilities")
D.5.1 | Immunity to change of frequency (RoCoF) |  |  | Art 13 1.(b)
| Frequency against time profiles for rate of change of frequency immunity |  | Figure 10: profiles for overfrequency and underfrequency, including for synchronous production technologies. with sliding measurement window of 500 ms: max Rocof = 2 Hz/sec |  | all units | no |  | declaration or certificate / test report | [7 empty] | 11.2.8 | 10.2.4.3
D.5.2 | Under-voltage ride through (UVRT) (voltage dips) |  |  | Art 14 3.(a) Art 17 3 Art 20 3.(a)
| Basic requirement for units < 1 MW only suitable for installations < 1MW (= type A) |  | no requirement (conformity with D.5.2 is optional) |  | units < 1 MW | no |  | declaration
|  |  | enter the real withstand capability to power dips in the field "Additional information" |  | units < 1 MW | no |  |  |  |  | (give information)
| Mandatory for units ≥ 1 MW (application in installations type B) OPTIONAL for units < 1MW ("type B ready": applicable in installations ≥ 1MW) | synchronous production technologies | power-generating unit must remain connected to the grid operating above the voltage-time profile in figure 11 |  | synchronous units ≥ 1 MW OPTIONAL for synchronous units < 1MW ("type B ready") | no | X | declaration or certificate / test report | [7 empty] | 11.2.5 | 10.2.3 | 4.6.2
|  |  | after a return from voltage to continuous operation domain, power is restored within 3 seconds to: - or min 90% of the power before the failure - or 90% of available power (smallest value of the 2) |  | synchronous units ≥ 1 MW OPTIONAL for synchronous units < 1MW ("type B ready") | no | X | declaration or certificate / test report | [7 empty] | 11.2.5 | 10.2.3 | 4.6.2
|  | non-synchronous generating technology (power park module) | power-generating unit must remain connected to the grid operating above the voltage-time profile in figure 12 |  | non-synchronous units ≥ 1 MW OPTIONAL for non-synchronous units < 1MW ("type B ready") | no | X | declaration or certificate / test report | [7 empty] | 11.2.5 | 10.2.3 | 4.6.3
|  |  | after a return from voltage to continuous operation domain, power is restored within 1 second to: - or min 90% of the power before the failure - or 90% of available power (smallest value of the 2) |  | non-synchronous units ≥ 1 MW OPTIONAL for non-synchronous units < 1MW ("type B ready") | no | X | declaration or certificate / test report | [7 empty] | 11.2.5 | 10.2.3 | 4.6.3
|  | Technology where short-circuit power at connection point affects immunity to voltage dips | Enter in field "additional information" the minimum short circuit power to comply with the UVRT requirements. |  | units ≥ 1 MW OPTIONAL for units < 1MW ("type B ready") | no | X | declaration or certificate / test report |  |  | (give information) |  |  |  |  | 11.2.5 | 10.2.3
| backup power systems |  | power-generating unit must remain connected to the grid operating above the voltage-time profile in figure 13 |  | ONLY for emergency group according to C10/11 §2.2.1 | yes |  | declaration or certificate / test report | [6 empty] | 5.9 | 11.2.5 | 10.2.3 | 4.6.3
D.5.3 | Over-voltage ride through (OVRT)
| not applicable in this edition |  | no requirement in this edition
D.6 | Power response to frequency deviations
D.6.1 | Power response to overfrequency |  |  | Art 13 2
| Power response to overfrequency according to EN 50549-1 and 50549-2 §4.6.1 completed or amended with the following parameters |  |  |  | all units | no |  | declaration
| Parameters dynamic step response for synchronous generating technology - table 12 |  | default maximum step response time of 30 s in EN 50549-1/2 is replaced by a dynamic step response as follows:
| step response time | for power increase | ≤ 5 minutes for an increase of active power of 20% Pmax (please note that the response should be as fast as technically possible, for example: a slow reaction is not applicable in the case of an increase shortly (few seconds) following a decrease phase) |  | synchronous units | no |  | certificate / test report | [5 empty] | 5.7.4.3 | 5.4.4 of 5.4.5 | 11.2.8 | 10.2.4.3 | 4.1.3
|  | for power decrease | ≤ 8 seconds for a decrease of active power of 45% Pmax |  | synchronous units | no |  | certificate / test report | [5 empty] | 5.7.4.3 | 5.4.4 of 5.4.5 | 11.2.8 | 10.2.4.3 | 4.1.3
| Settling time (tolerance band +- 10%) | for power increase | ≤ 6 minutes for an increase of active power (please note that the response should be as fast as technically possible, for example: a slow reaction is not applicable in the case of an increase shortly (few seconds) following a decrease phase) |  | synchronous units | no |  | certificate / test report | [5 empty] | 5.7.4.3 | 5.4.4 of 5.4.5 | 11.2.8 | 10.2.4.3 | 4.1.3
|  | for power decrease | ≤ 30 seconds for a decrease of active power |  | synchronous units | no |  | certificate / test report | [5 empty] | 5.7.4.3 | 5.4.4 of 5.4.5 | 11.2.8 | 10.2.4.3 | 4.1.3
| Alternative power gradient (both with frequency increases and decreases) for gas turbines and internal combustion engines | Pmax < 2 MW | minimum 1,11 % of Pmax per second |  | ONLY for gas turbines and internal combustion engines ≤ 2 MW, incapable of basic requirement | no |  | certificate / test report | [5 empty] | 5.7.4.3 | 5.4.4 | 11.2.8 | 10.2.4.3 | 4.1.3
|  | Pmax > 2 MW | minimum 0,33 % of Pmax per second |  | ONLY for gas turbines and internal combustion engines > 2 MW, incapable of basic requirement | no | X | declaration | [7 empty] | 11.2.8 | 10.2.4.3 | 4.1.3
| Parameters dynamic step response for non-synchronous generating technology - table 13 |  | default maximum step response time of 30 s in EN 50549-1/2 is replaced by a dynamic step response as follows:
| Step response time | for power increase | Wind generation: ≤ 5 seconds for an increase of active power of 20% Pmax (please note that the response should be as fast as technically possible, for example: at operating points below 50% of maximum power a slower reaction may apply, nonetheless, the response time shall not be more than 5 s) |  | ONLY for non-synchronous units on the basis of WIND energy | no |  | certificate / test report | [5 empty] | 5.7.4.3 | 5.4.4 of 5.4.5 | 11.2.8 | 10.2.4.3 | 4.1.3
|  |  | For the rest: ≤ 10 seconds for an increase of active power of 50% Pmax |  | non-synchronous units | no |  | certificate / test report | [5 empty] | 5.7.4.3 | 5.4.4 of 5.4.5 | 11.2.8 | 10.2.4.3 | 4.1.3
|  | for power decrease | ≤ 2 seconds for a reduction of active power of 50% Pmax |  | non-synchronous units | no |  | certificate / test report | [5 empty] | 5.7.4.3 | 5.4.4 of 5.4.5 | 11.2.8 | 10.2.4.3 | 4.1.3
| Settling time (tolerance band +- 10%) | for power increase | ≤ 30 seconds for an increase of active power |  | non-synchronous units | no |  | certificate / test report | [5 empty] | 5.7.4.3 | 5.4.4 of 5.4.5 | 11.2.8 | 10.2.4.3 | 4.1.3
|  | for power decrease | ≤ 20 seconds for a reduction of active power |  | non-synchronous units | no |  | certificate / test report | [5 empty] | 5.7.4.3 | 5.4.4 of 5.4.5 | 11.2.8 | 10.2.4.3 | 4.1.3
| If the unit reaches the minimum regulating level as the frequency continues to increase: maintain the minimum regulating level until a decrease in frequency results in a set point that is again above the minimum regulating level. |  |  |  | all units | no |  | certificate / test report | [5 empty] | 5.7.4.3 | 5.4.4 of 5.4.5 | 11.2.8 | 10.2.4.3 | 4.1.3
| restoration active power after deactivation frequency response (f < f1) |  | gradient of 10% Pmax per minute for recovery active power to available power |  | all units | no |  | certificate / test report | [5 empty] | 5.7.4.3 | 5.4.4 of 5.4.5 | 11.2.8 | 10.2.4 | 4.1.3
| parameter settings for power response to overfrequency - table 14 | Range | Setting
| Threshold frequency f1 | 50,2 Hz to 52 Hz | 50,2 Hz |  | all units | no |  | certificate / test report | [5 empty] | 5.7.4.3 | 5.4.4 of 5.4.5 | 11.2.8 | 10.2.4.3 | 4.1.3
| optional deactivation threshold fstop | 50,0 Hz to f1 | if implemented: deactivated |  | all units | no |  | declaration or certificate / test report | [5 empty] | 5.7.4.3 | 5.4.4 of 5.4.5
| Droop | 2% to 12% | 5% (40% Pref/Hz) |  | all units | no |  | certificate / test report | [5 empty] | 5.7.4.3 | 5.4.4 of 5.4.5 | 11.2.8 | 10.2.4.3 | 4.1.3
| Intentional delay | 0 s to 2 s | 0 s * |  | all units | no |  | certificate / test report | [5 empty] | 5.7.4.3 | 5.4.4 of 5.4.5 | 11.2.8 | 10.2.4.3 | 4.1.3
* The actual default setting is 0 s. Nevertheless, for units without remote monitoring and control, this value could be reviewed as a result of the evaluation of the risk of having unintended island operations.
| protection of settings (password, seal, …) |  | Enter in the field "Additional information" which type of seal |  | all units | no |  | declaration |  |  | (give information)
| alternative for droop in NC RfG Art. 13 2.(b) (automatic disconnection and reconnection) |  | not allowed | Art. 13 2.(b) | all units | no |  | declaration
| Minimum "state of charge" for energy storage systems |  | see text: agreement with DSO |  | ONLY for energy storage systems | no |  | declaration
D.6.2 | Power response to underfrequency
| according to EN 50549-1 or EN 50549-2 §4.6.2 completed or amended with the following parameters |  |  |  | MANDATORY for energy storage systems (from 01/05/2020) OPTIONAL for all other units: if activated, compulsory in accordance with D.6.2 | no |  | declaration
| Minimum "state of charge" for energy storage systems |  | see text: agreement with DSO |  | ONLY for energy storage systems (from 01/05/2020) | no |  | declaration
| characteristics for dynamic step response |  | default maximum step response time of 30 s in EN 50549-1/2 will be replaced by dynamic step response as in D.6.1 |  | energy storage systems (from 01/05/2020) OPTIONAL: all other units | no |  | declaration
| Parameter - table 15 | Range | Setting
| Threshold frequency f1 | 49,8 Hz to 46 Hz | 49,8 Hz |  | energy storage systems (from 01/05/2020) OPTIONAL: all other units | no |  | certificate / test report | [5 empty] | 5.7.4.3 | 5.4.6 OF 5.4.7 | 11.2.8 | 10.2.4.3 | 4.1.3
| Droop | 2% to 12% ** | For energy storage systems: 2 % (100% Pref/Hz) ** |  | energy storage systems (from 01/05/2020) | no |  | certificate / test report | [5 empty] | 5.7.4.3 | 5.4.6 OF 5.4.7 | 11.2.8 | 10.2.4.3 | 4.1.3
|  |  | For all other power-generating units: 5 % (40% Pref/Hz) |  | OPTIONAL: all units other than energy storage systems | no |  | certificate / test report | [5 empty] | 5.7.4.3 | 5.4.6 OF 5.4.7 | 11.2.8 | 10.2.4.3 | 4.1.3
| Intentional delay | 0 s to 2 s | 0 s * |  | energy storage systems (from 01/05/2020) OPTIONAL: all other units | no |  | certificate / test report | [5 empty] | 5.7.4.3 | 5.4.6 OF 5.4.7 | 11.2.8 | 10.2.4.3 | 4.1.3
* The actual default setting is 0 s. Nevertheless, for units without remote monitoring and control, this value could be reviewed as a result of the evaluation of the risk of having unintended island operations.
| ** Considering the principles of Art. 15.3 of the Emergency and Restoration Network Code[31], a droop if 1 % is requested for energy storage systems having a maximum power ≥ 1 MW. If this is technically not possible, alternatively a droop of 2% is accepted. |  |  |  | energy storage systems ≥ 1 MW (from 01/05/2020) | no | X | declaration
| In application of the article 15.3 (b) of the Emergency and Restoration Network Code, an energy storage system having a maximum power ≥ 1 MW shall disconnect prior to the activation of the automatic low frequency demand disconnection scheme (starting at 49Hz) if it is still in charging mode. The disconnection threshold can be fixed randomly within the range [49Hz 49,2 Hz]. |  |  |  | energy storage systems ≥ 1 MW (from 01/05/2020) | no | X | declaration
| protection of settings (password, seal, …) |  | Enter in the field "Additional information" which type of seal |  | energy storage systems from 01/05/2020 OPTIONAL: all other units | no |  | declaration |  |  | (give information)
D.7 | Power response to voltage changes
D.7.1 | Voltage support by reactive power |  |  | Art 17 2.(a,b) Art 20 2.(a)
| according to EN 50549-1 or EN 50549-2 §4.7.2 completed or amended with the following parameters |  |  |  | all units (< 1MW: from 01/05/2020) | no |  | declaration
| Requirement provided in the power-generating unit itself (to be checked at the time of homologation) or at another level (to be checked during implementation)? Specify in the box "additional information" : "yes (provided in the power-generating unit itself)" or "no (provided on another level - to check during commissioning". If the voltage support by reactive power is not provided in the unit itself, section D.7.1 does not apply for homologation of the unit. |  |  |  | all units (< 1MW: from 01/05/2020) | no |  | declaration |  |  | (give information)
| reactive power range + control modes | small power-generating units - units ≤ 10kVA three-phase - units ≤ 5kVA single-phase ONLY to be used in a "small power-generating plant " as defined in §4.1.7 of C10/11 - see D.7.1.1 | reactive power range: - when the voltage≤ 105% Un: cos phi = 1 (Q=0) - when the voltage>105% Un: free operation with 1≥ cos phi > 0,9 (under-excited). no over-excited operation allowed |  | small power-generating units (from 01/05/2020) - units ≤ 10kVA three-phase - units ≤ 5kVA single-phase ONLY to be used in "small power-generating units" according to C10/11 §4.1.7 | no |  | certificate / test report | [5 empty] | 5.7.2.5 | 5.4.8
|  | units ≤ 250kVA | reactive power range as indicated in figure van EN 50549-1 §4.7.2 from 0,9 over-excited to 0,9 under-excited) Control modes as indicated in EN 50549-1 §4.7.2: - set point Q - Q(U) - Cos φ set point - Cos φ (P) |  | units ≤ 250kVA (from 01/05/2020) | no |  | certificate / test report | [5 empty] | 5.7.2.5 | 5.3.8 | 11.2.4 | 10.2.2.4 | 4.2.2-6
|  | units > 250 kVA OPTIONAL for units ≤ 250kVA | Reactive power range as indicated in figure of EN 50549-2 §4.7.2 (of-0,33 Q/PD to 0,33 Q/PD) Control modes as indicated in EN 50549-2 §4.7.2: - set point Q - Q(U) - Q(P) - Cos φ set point - Cos φ (P) |  | units > 250kVA (< 1MW: from 01/05/2020) OPTIONAL for units ≤ 250kVA | no |  | certificate / test report | [5 empty] | 5.7.2.5 | 5.4.8 | 11.2.4 | 10.2.2.4 | 4.2.2-6
|  | additional requirement for units ≥ 1 MW (application in installations type B) OPTIONAL for units < 1MW ("type B ready": applicable in installations ≥ 1MW) | Control modes: - mandatory alternative for Q(U): equipment with a permanent automatic excitation control system (see text C10/11). - Setpoint: selectable in the continuous operating domain for the voltage (D.4.3). (selection of setpoint by DSO) |  | synchronous units ≥ 1 MW OPTIONAL for synchronous units < 1MW ("type B ready") | no | X | certificate / test report | [5 empty] | 5.7.2.5 | 5.4.8 | 11.2.4 | 10.2.2.4 | 4.2.2-6
|  |  | Equipment must be expandable to allow remote selection of set point |  | synchronous units ≥ 1 MW OPTIONAL for synchronous units < 1MW ("type B ready") | no | X | declaration
|  | EXCEPTION for CHP ≤ 150 kVA | reactive power range: From 0,95 over-excited to 0,95 under-excited |  | ONLY for WKK ≤ 150 kVA (from 01/05/2020) | no |  | certificate / test report | [5 empty] | 5.7.2.5 | 5.4.8 | 11.2.4 | 10.2.2.4 | 4.2.2-3
|  | EXCEPTION for induction generator ≤ 16A | reactive power range: Operating with active power factor > 0,95 Control modes: none |  | ONLY for induction generators ≤ 16A (from 01/05/2020) | no |  | certificate / test report | [5 empty] | 5.7.2.5 | 5.4.8 | 11.2.4 | 10.2.2.4 | 4.2.2-3
|  | EXCEPTION for induction generator > 16A | Reactive power range: from ,95 under-excited to 1 Control modes: Only Cos φ set point at PD |  | ONLY for induction generators > 16A (< 1MW: from 01/05/2020) | no |  | certificate / test report | [5 empty] | 5.7.2.5 | 5.4.8 | 11.2.4 | 10.2.2.4 | 4.2.2-6
|  | EXCEPTION for linear generator | reactive power range: Operating with active power factor > 0,95 Control modes: none |  | ONLY for linear generators (< 1MW: from 01/05/2020) | no |  | certificate / test report | [5 empty] | 5.7.2.5 | 5.4.8 | 11.2.4 | 10.2.2.4 | 4.2.2-3
|  | EXCEPTION for emergency groups according to C10/11 §2.1.1 | reactive power range: power factor must be as close to 1 and not below the limit of 0,85 in-parallel operation. Control modes: none |  | ONLY for emergency groups according to C10/11 §2.2.1 (< 1MW: from 01/05/2020) | yes |  | certificate / test report | [5 empty] | 5.7.2.5 | 5.4.8 | 11.2.4 | 10.2.2.4 | 4.2.2-3
| State in field "Additional information" the real technical possibilities of the power-generating unit for the exchange of reactive power. |  |  |  | all units (< 1MW: from 01/05/2020) | no |  |  |  |  | (give information)
| protection of settings (password, seal, …) |  | Enter in the field "Additional information" which type of seal |  | all units (< 1MW: from 01/05/2020) | no |  | declaration |  |  | (give information)
D.7.2 | Voltage related active power reduction P(U)
| OPTIONAL (recommended). If implemented, Mandatory according to EN 50549-1 or EN50549-2 §4.7.3 |  | If implemented, enter in box "additional information" which standard (EN 50549-1 or EN 50549-2) has been used. |  | OPTIONAL for all units (recommended) | yes |  | declaration |  |  | (give information)
D.7.3 | Provision of additional fast reactive current during faults and voltage steps |  |  | Art. 20 2.(b)
| non-synchronous units < 1 MW |  | Capacity: no requirement If capacity is available: standard deactivation |  | non-synchronous units < 1 MW | yes |  | declaration or certificate / test report | [7 empty] | 11.2.5.5-6 | 10.2.3.2-4 | 4.6.3
| non-synchronous units ≥ 1 MW OPTIONAL for non-synchronous units < 1MW ("type B ready") | maximum power ≥ 1 MW | behaviour according to EN 50549-2 §4.7.4.2.1 + additional information D.7.3 Function deactivated by default. |  | non-synchronous units ≥ 1 MW OPTIONAL for non-synchronous units < 1MW ("type B ready") | yes | X | declaration or certificate / test report | [7 empty] | 11.2.5.5-6 | 10.2.3.2-4 | 4.6.3
D.8 | Connection and reconnection |  |  | Art 13 7 Art 14 4
| according to EN 50549-1 or EN 50549-2 §4.10 completed or amended with the following parameters |  | behaviour according to EN 50549-1 or EN 50549-2 §4.10 |  | all units | yes |  | declaration
| Table 16 – conditions for automatic connection and reconnection | Parameter
| Reconnection after tripping of the interface protection relay | Underfrequency | 49,9 Hz |  | all units (< 1MW: from 01/05/2020) | yes |  | certificate / test report | [5 empty] | 8.3.1 | 5.6 | 11.2.11 | 10.4.2 | 4.5.2
|  | Overfrequency | 50,1 Hz |  | all units (< 1MW: from 01/05/2020) | yes |  | certificate / test report | [5 empty] | 8.3.1 | 5.6 | 11.2.11 | 10.4.2 | 4.5.2
|  | Undervoltage | 85% Un (LV connection) of 90% Uc (HV connection) |  | all units (< 1MW: from 01/05/2020) | yes |  | certificate / test report | [5 empty] | 8.3.1 | 5.6 | 11.2.11 | 10.4.2 | 4.5.2
|  | Overvoltage | 110% Uref where Uref= - LV connection: Un = 230 V - HV connection: Uc = declared voltage |  | all units (< 1MW: from 01/05/2020) | yes |  | declaration or certificate / test report | [5 empty] | 8.3.1 | 5.6
|  | Observation time | 60 s |  | all units (< 1MW: from 01/05/2020) | yes |  | certificate / test report | [5 empty] | 8.3.1 | 5.6 | 11.2.11 | 10.4.2 | 4.5.2
|  | Maximum active power increase gradient | 10%/min* |  | all units (< 1MW: from 01/05/2020) | yes |  | certificate / test report | [5 empty] | 8.3.1 | 5.6 | 11.2.11 | 10.4.1 | 4.1.4
|  | EXCEPTION: Units that cannot apply this gradient must provide for an additional delay. |  |  | EXCEPTION for units not capable of required gradient (< 1MW: from 01/05/2020) | yes |  | declaration
| Normal operation starting | Underfrequency | 49,9 Hz |  | all units | yes |  | certificate / test report | [5 empty] | 8.3.1 | 5.6 | 11.2.11 | 10.4.1 | 4.5.1
|  | Overfrequency | 50,1 Hz |  | all units | yes |  | certificate / test report | [5 empty] | 8.3.1 | 5.6 | 11.2.11 | 10.4.1 | 4.5.1
|  | Undervoltage | 85% Uref where Uref= - LV connection: Uref = Un = 230 V - HV connection: Uref = Uc = declared voltage |  | all units | yes |  | certificate / test report | [5 empty] | 8.3.1 | 5.6 | 11.2.11 | 10.4.1 | 4.5.1
|  | EXCEPTION if distinction between connection and reconnection is not possible | 90% Uc (HV connection) |  | EXCEPTION for units technically incapable of distinguishing between coupling and re-coupling | yes |  | declaration or certificate / test report | [7 empty] | 11.2.11 | 10.4.1 | 4.5.1
|  | Overvoltage | 110% Uref where Uref= - LV connection: Uref = Un = 230 V - HV connection: Uref = Uc = declared voltage |  | all units | yes |  | certificate / test report | [5 empty] | 8.3.1 | 5.6 | 11.2.11 | 10.4.1 | 4.5.1
|  | Observation time | 60 s |  | all units | yes |  | declaration or certificate / test report | [5 empty] | 8.3.1 | 5.6
|  | Maximum active power increase gradient | 20%/min |  | all units | yes |  | certificate / test report | [5 empty] | 8.3.1 | 5.6 |  | 10.4.1 | 4.1.4
D.9 | Ceasing production and reduction of active power on set point
D.9.1 | Ceasing production of active power |  |  | Art 13 6
| according to EN 50549-1 AND EN 50549-2 §4.11.1 completed or amended with the following parameters |  |  |  | units > 800W | no |  | declaration
| units ≤ 800 W | no requirement |  |  | units ≤ 800 W ONLY for use in module ≤ 800 W | no |  | declaration
| units > 800 W OPTIONAL for units ≤ 800 W | a logic interface (input port) | stop active power within 5 seconds after receiving an instruction on the input port |  | units > 800W | no |  | declaration
|  |  | Principle: contact instead of communication protocol ? Fill in field "additional information". |  | units > 800W | no |  | declaration |  |  | (give information)
D.9.2 | Reduction of active power on set point |  |  | Art 14 2
| according to EN 50549-2 §4.11.2 completed with the following parameters |  |  |  | units ≥ 1 MW OPTIONAL for units < 1MW ("type B ready") depending on REGION: also for unit > 250kVA if required by DSO | no |  | declaration
| Requirement provided in the power-generating unit itself (to be checked at the time of homologation) or at another level (to be checked during implementation)? Specify in the box "additional information" : "yes (provided in the power-generating unit itself)" or "no (provided on another level - to check during commissioning". If the reduction of active power by setpoint is not provided in the unit itself, section D.9.2 does not apply for homologation of the unit. |  |  |  | units ≥ 1 MW OPTIONAL for units < 1MW ("type B ready") depending on REGION: also for unit > 250kVA if required by DSO | no | X | declaration
| units ≥ 1 MW OPTIONAL for units < 1MW ("type B ready") Depending on REGION: also for unit > 250kVA if required by DSO | Reduction of active power on set point | From maximum power to minimum regulating level with a maximum increment of 10%. |  | units ≥ 1 MW OPTIONAL for units < 1MW ("type B ready") depending on REGION: also for unit > 250kVA if required by DSO | no | X | certificate / test report | [5 empty] | 5.7.4.1 | 5.4.3 | 11.2.7 | 10.2.4.1 | 4.1.2
|  |  | Maximum 0,66% Pn/s and minimum 0,33% Pn/s |  | units ≥ 1 MW OPTIONAL for units < 1MW ("type B ready") depending on REGION: also for unit > 250kVA if required by DSO | no | X | certificate / test report | [5 empty] | 5.7.4.1 | 5.4.3 | 11.2.7 | 10.2.4.1 | 4.1.2
|  |  | Disconnection is allowed if under minimum regulating level. |  | units ≥ 1 MW OPTIONAL for units < 1MW ("type B ready") depending on REGION: also for unit > 250kVA if required by DSO | no | X | certificate / test report | [5 empty] | 5.7.4.1 | 5.4.3 | 11.2.7 | 10.2.4.2 | 4.1.2
|  |  | Remote service is optional (see text) |  | units ≥ 1 MW OPTIONAL for units < 1MW ("type B ready") depending on REGION: also for unit > 250kVA if required by DSO | no | X | declaration
| additional equipment for a remote operation of this reduction by DSO |  | see D.10 |  | units ≥ 1 MW OPTIONAL for units < 1MW ("type B ready") depending on REGION: also for unit > 250kVA if required by DSO | no | X | declaration
D.10 | Communication – Remote monitoring and control |  |  | Art. 14 5.d
| units ≥ 1 MW OPTIONAL for units < 1MW ("type B ready") Depending on REGION: also for unit > 250kVA if required by DSO |  | necessary functionalities regarding remote monitoring and control to meet the requirements of section 7.13 in C10/11. |  | units ≥ 1 MW OPTIONAL for units < 1MW ("type B ready") depending on REGION: also for unit > 250kVA if required by DSO | no | X | declaration
EXPLANATIONS FOR COMPLETING THE CHECKLIST IN ANNEX D AND FOR COMPILING THE TECHNICAL FILE | [8 empty] | compliant
non-compliant
Column | Title | Remarks | [6 empty] | non applicable
B - C | Reference in annex D of C10/11 | Reference to the relevant section in the text of C10/11
D | Characteristic | See text C10/11 for a full description.
E | Requirement - black = mandatory - blue = additional information needed in column M | See text C10/11 for a full description.
F | Reference NC RfG | If applicable, the relevant section of the European Network Code Requirements for Generators is provided.
G - H - I | Applicable on what units? | A distinction is made here between the general rule, and specifically the following properties: - requirements to which an exception applies for emergency groups (backup power systems) in accordance with the definition in C10/11 §2.1.1 - requirements specific to installations type B according to the NC RfG, in Belgium these installations are ≥ 1 MW This information is also included in the C10/26 list in tab 2.
J | Required proof of conformity | The following three options are possible:
1. A declaration of honour by the manufacturer regarding conformity with the requirement is sufficient. In this case, the filling in of column K in combination with the signing of the conformity declaration in the first tab applies as the declaration of honour of the manufacturer. There is no need for a separate document for this.
2. A certificate or test report is required. In this case, columns P - Q - R - S - T contain suggestions for relevant sections in relevant standards. See also remark at P - Q - R - S -T (non-exhaustive, indicative list).
The exact requirements of C10/11 can deviate from the international standards: even if a certificate of test report based on an international standard is required, the exact requirement of C10/11 prevails in case it deviates. Therefore, by indicating "compliant" in column K (C10/11 compliant) the manufacturer declares that the power-generating unit is compliant with the requirements of C10/11, including any possible deviations from the references in columns P - Q - R - S - T .
It is allowed to propose certificates or test reports based on other normative references, on the conditions that - the equivalence is proved by the manufacturer; - they are compliant with the conditions for a valid proof of conformity as mentioned below.
3. Either a declaration of honour, or a certificate / test report is required. This choice is given if there is only a suitable normative reference available either for connections on LV (columns P and Q) , or for connections on HV (column R - S - T). A certificate or test report is always preferred if possible or available.
Conditions for a valid proof of conformity: - to be available in Dutch, French, English or German. Other languages are not accepted. - to be available as a separate document in the technical file. Hyperlinks to online documents without the presence of the document itself, or to web pages, are not accepted as valid proof of conformity. - a document with a unique file name (reference), included in the list of proofs of conformity in tab 4, together with an explanation of the content of the document. - additional: conditions for a valid certificate or test report: see tab 1 (declaration of conformity) - Certificates have been drawn up by an EN 45011 (or ISO 17065:2012) certification body accredited for these materials. - Test reports have been drawn up by an ISO 17025:2005 or ISO 17065:2012 laboratory accredited for these tests.
K | C10/11 Compliant? | The filling in of column K in combination with the signing of the declaration of conformity in the first tab applies as the declaration of honour of the manufacturer concerning the conformity of the units with the relevant paragraph in annex D of C10/11.
L | Manufacturer’s reference of proof of conformity | Each piece of evidence used to demonstrate the required conformity shall have a unique reference number, specified in this column. However, the same piece of evidence may be used as evidence for more than one requirement if its contents permit it. Each supporting document mentioned in this column must be completed in the 4th tab "proofs of conformity" together with an explanation, and must be present as a separate document in the technical file. See tab 4 "Proofs of conformity" for the conditions for a valid proof of conformity.
M | Additional information | Here the manufacturer has room for explanations: - mandatory information if indicated in column E - a free explanatory note if the manufacturer feels it necessary.
N | Evaluation Synergrid | This column can be filled in by Synergrid during the study of the homologation application.
O | Explanation Synergrid | This column can be filled in by Synergrid during the study of the homologation application.
P - Q - R - S | Relevant standards for proofs of conformity indicative, non-exhaustive list | For those characteristics for which a certificate or a test report is required, these columns shall indicate the relevant paragraphs of applicable standards. This list is not exhaustive: the manufacturer is free to submit a certificate of conformity via another standard, under the condition that it is compliant with the conditions for a valid proof of conformity, as mentioned above (explanation for column J).

## 4. proofs of conformity
0
POWER-GENERATING UNITS TO BE HOMOLOGATED FOR THE LIST C10/26 ACCORDING TO THE REQUIREMENTS OF ANNEX D OF THE TECHNICAL PRESCRIPTION C10/11 ed2.4 (15/10/2025)
4. Composition of the technical file: list of document references of the proofs of conformity referred to in the checklist in annex D.
GLV |  | (brand name) | (series name)
GLV ed2.1.4 (10/2025)
No. | Type of document | Manufacturer-references of the proofs of conformity according to the references given in column L of the checklist annex D | Description
datasheet
test report
other