## ReadMe
POWER-GENERATING UNITS TO BE HOMOLOGATED FOR THE LIST C10/26
ACCORDING TO THE REQUIREMENTS OF ANNEX D OF THE TECHNICAL PRESCRIPTION C10/11 ed2.4 (15/10/2025)
Frequently asked questions
The checklist in sheet 3 is usually covered by one test report, valid for all units in sheet 2.
If sheet 2 contains two (or more) series, covered by different test reports (one report for each series), there should also be separate applications.
If sheet 2 contains two (or more) series, covered by the same test report because the units/series are technically related, they can be treated in the same request, and share sheet 3.
There is no need for C10/11-specific test reports, an international test report is acceptable.
Preference for international test reports based on EN50549-01, -02 or -10.
Proofs of conformity: declaration versus test report.
When the checklist indicates "declaration" in column J, no separate declaration is needed.
Completion of column K is considered to be a declaration of honour by manufacturer.
Specifically for gensets :
If the genset as a whole has no nameplate, please mention the reference of the motor and generator/alternator for each unit in sheet 2.
This is necessary to allow an identification of the set as mentioned in sheet 2 on site.
For gensets with a different power value in prime and standby mode, please specify the mode for which the power values are valid in sheet2 (for example between brackets).
If needed, for each genset there can be two separate lines in sheet 2, for prime and standby mode, with the corresponding power values.
Specifically for wind turbines :
For wind turbines with a different power value depending on the operating mode, please specify the mode for which the power values are valid in sheet2 (for example between brackets).
Rebranding of an OEM product under a different brand name - procedure |  |  |  | See model declaration in sheet "rebranding - OEM declaration"
When you commercialise an already homologated unit or series under a different brand name, your homologation request needs to be linked to the original units(s), since they are technically identical.
For this, we need a declaration of honour about equivalence.
| 1 | A model declaration is available in this file, see sheet “rebranding - OEM declaration”.
It is mandatory to use this template.
| 2 | The declaration will allow us to link unambiguously both the original and the rebranded unit(s).
This will simplify the homologation study, since the test reports can be replaced by this declaration.
| 3 | The declaration will need to be signed electronically by both parties: the original manufacturer, and the rebranding company.
This will also confirm the OEM manufacturer’s consent to the rebranding of his unit(s).
When you introduce a request, fill in the sheet “rebranding - OEM declaration” in this file.
Create a pdf file from this sheet, and upload this filled-in but unsigned pdf document in "proofs".
Synergrid will then launch the electronic signing process for both parties. This process is similar to the signature of an approved application.
For a homologation request of a rebranded series, we need at least 3 documents:
| 1 | A homologation-request by means of this excel file, but only the sheets 1 GLV, 2 list PGU and the sheet “rebranding - OEM declaration” need to be filled in.
In sheet 2 the brand name and references of the rebranded units must be filled in.
The “rebranding - OEM declaration” serves as replacement for sheet 3 and corresponding test report(s)
| 2 | The commercial datasheets of the rebranded units
| 3 | The unsigned pdf version of the “rebranding - OEM declaration” as explained above.
Firmware-limitations and units specifically for Belgium
The prescription C10/11 explicitly mentions that firmware or software limitation is not taken into consideration to determine the maximum power, see C10/11 §4.1.8:
That is why we check the maximum apparent power values in the test reports, in the datasheets and on the nameplates: they should all be corresponding.
One unique product reference can only have one unique maximum apparent power value (in Belgium and in other countries).
It is not allowed in Belgium to commercialise one product that could have a higher maximum apparent power value in another country.
Firmware- of software limitation is not forbidden, but the limited value will not be taken into consideration.
However, it is possible to commercialise a separate series for Belgium based on the original one, but with different power values, and to have these homologated.
They would have to be commercially separate models:
| 1 | Unique product reference, different from the original unit so that the difference is clear for everyone.
This can be done for example by creating a version with "-BE" extension in the unit reference.
A product reference is like a password: each character should be correct. The product reference in itself should make it possible to distinguish between both versions.
| 2 | Unique nameplate, with the new unit reference and power values.
| 3 | Commercial datasheet mentioning this model (it can be a new one, or an updated one also containing the originally homologated units).
| 4 | Declaration of honour of the manufacturer, stating the technical equivalence of the units, so that the test reports and technical file based on annex D can also be valid for this unit.
Power limits in Belgium in monophase connections to the grid, and Delta-grids (3x230V).
For most Belgian distribution grid operators, in a monophase connection to the grid, the maximum apparent power (in VA) that can be installed is 5000VA.
See C10/11 §4.1.7 for the definition of a "small power generating installation".
That is why monophase units with a maximum apparent power exceeding 5000VA are marked with a pink background.
Their application in monophase connections is limited to some grid operators only:
Situation on 11/2024, see website of the grid operators for the most recent information.
Installation > 5kVA in monophase connections
|  | Fluvius | Forbidden
|  | Sibelga | Forbidden (since 17/10/2024, publication date CCLB111)
|  | Resa | Accepted if ≤ 10kVA
|  | ORES | Forbidden
However, monophase units with a maximum power exceeding 5kVA can be used in threephase grid connections on the condition that the power balance between phases is respected.
See C10/11 §8.2.5 and §7.6.7 (or §7.11.2 for storage).
They can be particularly useful in threephase grids of Delta type (3x230V without neutral conductor) since most 3-phase inverters cannot work on this type of network.
There is still a considerable amount of networks in Belgium of this type, however the share is decreasing each year (gradual conversion to 3x400V+N networks)
Homologation of plug&play devices
Plug&play manufacturer’s information C10/26:
| Nederlands | https://www.synergrid.be/images/downloads/INFO_fabrikanten_2024.11_C10-11_ed2.3_plug-and-play_NL.pdf
| English | https://www.synergrid.be/images/downloads/INFO_fabrikanten_2024.11_C10-11_ed2.3_plug-and-play_FR.pdf
| Français | https://www.synergrid.be/images/downloads/INFO_fabrikanten_2024.11_C10-11_ed2.3_plug-and-play_EN.pdf

## rebranding - OEM declaration
C10/26 - DECLARATION OF EQUIVALENCE for rebranding of homologated power-generating units
Agreement between Original Manufacturer and Rebranding Company.
The undersigned, |  | Original Manufacturer (OEM): |  |  | Represented by:
|  | Address: |  |  | Country:
email:
|  | Country: |  |  | Telephone:
The undersigned, |  | Rebranding company: |  |  | Represented by:
|  | Address: |  |  | Country:
email:
|  | Country: |  |  | Telephone:
The Original Manufacturer hereby declares that :
- The Rebranding Company has permission to market the products - manufactured by the Original Manufacturer - under its own label and product name.
- The original products have successfully obtained a C10/26-homologation and are included in the list C10/26 of Synergrid. See list below.
- The original products and the rebranded product are technically identical. Thus, the technical information provided by the Original Manufacturer to Synergrid for the
homologation of the original products also applies to the rebranded products. This declaration replaces the required proof of conformity for the rebranded series.
| ORIGINAL UNITS |  |  |  | EQUIVALENT REBRANDED UNITS
| SYNERGRID reference number (GLVxxx-yy-zzzz) | BRAND NAME | Name of the product SERIES | REFERENCE of the model / type of the unit | BRAND NAME | Name of the product SERIES | REFERENCE of the model / type of the unit
| Original Manufacturer's signature: |  | Digitally signed, see last page |  | Rebranding Company's signature: |  | Digitally signed, see last page

## 1 GLV
GLVxxx-yy |  | (brand name) | (series name)
C10/26 - DECLARATION OF CONFORMITY for power-generating units GLV ed2.4.1 (04/2026)
for compliance with annex D "Technical basic requirements regarding the power-generation units"of the Synergrid prescription C10/11 ed2.4 (15/10/2025).
The undersigned, |  | Manufacturer: |  | Represented by:
|  | Address: |  | Country:
email:
|  | Country: |  | Telephone:
Hereby declares that each power generating unit completed in the list in tab 2 'list of power-generating units' of this homologation application complies with the following conditions:
1. The power-generating units comply with the relevant requirements of the Synergrid prescription C10/11 ed2.4 (15/10/2025), mainly set out in annex D "Technical basic requirements regarding the power-generation units".
2. In order to substantiate this, a technical file (see tab 3 "checklist annex D") has been submitted for the product series of the 'C10/26 list of power-generating units' of this homologation application. The technical file shall be drawn up on the basis of the checklist Annex D of C10/11, duly and correctly completed by the manufacturer, accompanied by all the required proof of conformity.
2.1 For technical requirements for which the required proof of conformity (column J in checklist annex D) is a declaration of honour by the manufacturer, no additional documents are needed. By signing and dating this declaration of conformity, the manufacturer declares the correctness of the information (compliant / non-compliant / not applicable) provided by him or her in columns K, L and M of this checklist.
2.2. For technical requirements for which the required proof of conformity (column J in checklist Annex D) is a test report, the necessary test reports are available in the application at Synergrid. Test reports have been established by an ISO 17025:2005 or ISO 17065:2012 laboratory accredited for these tests.
Homologated by Synergrid on:
Manufacturer's signature: |  | Digitally signed, see last page |  | Synergrid signature: | Digitally signed, see last page
Please check ReadMe
before answering

## 2 list PGU
POWER-GENERATING UNITS TO BE HOMOLOGATED FOR THE LIST C10/26 ACCORDING TO THE REQUIREMENTS OF ANNEX D OF THE TECHNICAL PRESCRIPTION C10/11 ed2.4 (15/10/2025)
2. C10/26 list with power-generating units in accordance with annex D of C10/11 ed2.4 (15/10/2025)
GLVxxx-yy
checklist ed2.4.1 (04/2026)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | [5 empty] | 12 |  |  |  | 13 | [5 empty] | 14 | 15
SYNERGRID reference number (GLVxxx-yy-zzzz) | BRAND NAME | Name of the product SERIES | REFERENCE of the model / type of the unit | FIRMWARE VERSION | ONLY for units (suitable for) energy storage: Name and reference of the power control system |  | POWER |  | 1-phase or 3-phase | ADDITIONAL CHARACTERISTICS | [5 empty] | LIMITATIONS |  |  |  | APPLICATION
[7 empty] | Pac,r rated (active) power (W) | Smax maximum apparent power (VA) |  | D.3 | (...) | D.4.1 | D.6.2 | D.7.2 | () | D.7.1 | D.4.3 | D.9.1 | (...) | [6 empty] | Additional information | Synergrid homologation approval date
[5 empty] | Only for “Small” storage PGU’s : Power control system type EnFluRi (name), and/or use of P1 port of smart meter of DSO (indication “P1”). | All other (bigger) storage PGU’s : Other power control system (name) |  |  |  | integrated automatic separation system | RfG type B or "RfG type B ready" = suitable for use in installation ≥ 1MW | additional operating frequency range (51,5 Hz - 52,5 Hz) | power response to underfrequency | active power reduction P(U) | compliant power control system provided (e.g. EnFluRi) | only homologated for "small power-generating installations" | only homologated for connection to HV-network | only homologated for use in module < 800W | only homologated as a backup power system according to §2.1.1 | Solar energy | Wind energy | CHP (combined heat & power) | Energy storage | Backup power system | Other
[28 empty] | 0 | 0 | 0
[28 empty] | 0 | 0 | 0
[28 empty] | 0 | 0 | 0
[28 empty] | 0 | 0 | 0
[28 empty] | 0 | 0 | 0
[28 empty] | 0 | 0 | 0
[28 empty] | 0 | 0 | 0
[28 empty] | 0 | 0 | 0
[28 empty] | 0 | 0 | 0
[28 empty] | 0 | 0 | 0
[28 empty] | 0 | 0 | 0
[9 empty] | 1-phase | [16 empty] | Plug&play
[9 empty] | 3-phase | [16 empty] | Suitable for V2G
Generator (gas)
Generator (hydro)
Generator (diesel)
Generator (biomass)
EXPLANATIONS FOR THE COMPLETION OF THE TABLE
Column | Title | Remarks
1 | SYNERGRID reference | In the case of a positive homologation, each C10/26-homologated power-generating unit is given a unique Synergrid reference number:
| number | xxx = unique reference or the manufacturer
| (GLVxxx-yy-zzzz) | yy = serial number of manufacturer xxx's record xxx
zzzz = unique unit reference for the manufacturer xxx
Note : "GLV" is the internal Synergrid-abbreviation for Declaration of Conformity, based on the Dutch word "Gelijkvormigheidsverklaring".
2 | Brand name | Brand name under which the unit is marketed on the Belgian market.
3 | Name of the product series | Name of the product range. Note: For each separate product range (or each group of units with common characteristics) a separate checklist according to Appendix D is required (sheet 3) together with the corresponding conformity proof documents. Only series covered by the same test report (and thus technically related) can be grouped in the same request, otherwise a separate request has to be introduced.
4 | Reference of the model / type of the unit | Unique product name or reference. Units of the same product range must be unequivocally distinguished from each other through this name or reference.
5 | Firmware version | Reference of the firmware version of the unit.
6 | power control system type EnFluRi | This case is only applicable for units (suitable for) energy storage, provided with a power control system of type EnFluRi: Name and reference of the power control system of type EnFluRi, compliant to the requirements in C10/11 §4.1.7 and §7.11.2.1
7 | other power control system | This case is only applicable for units (suitable for) energy storage, provided with a power control system of another type than EnFluRi: Name and reference of the power control system, compliant to the requirements in C10/11 §7.11.2.2
8 | Pac,r rated (active) power (W) | Active (electrical) power in W at the terminals of the unit, as stated on the technical sheet / data sheet / brochure and nameplate. (For photovoltaic inverters: see also definition in §3.2.5 of IEC 62894 2016-11)
9 | Smax - maximum apparent power (VA) | Maximum apparent (electrical) power at the terminals of the unit, as stated on the certificate / the test report / the technical sheet / data sheet / brochure.
10 | 1-phase or 3-phase | Indicate whether the unit is single- or three-phase. This characteristic refers to the unit itself, not to the nature of the connection to the distribution network to which the unit can be connected.
11 | Additional characteristics | In these columns optional additional characteristics of the units are indicated, following the information in checklist annex D and the corresponding technical file. Put an "X" at each relevant additional characteristic. Note: Only units < 1 MW that are "type B ready" may be applied in an installation ≥ 1 MW (installation "type B" according to the European Network Code RfG). A unit < 1 MW is only "type B ready" if it complies with all optional properties ticked in column I of the checklist Annex D.
12 | Limitations | These columns specify limitations of the units to their application in certain types of installations, in accordance with the information in the checklist in annex D and the corresponding technical file. Put an "X" to each relevant limitation.
13 | Application | Indicate the applications for which the unit is suitable. Include an "X" with each application for which the unit can be used.
14 | Additional information | Additional information about the application of the unit(s): Plug&play, Suitable for V2G, Generator (gas), Generator (hydro), Generator (diesel), Generator (biomass), … .
15 | Synergrid homologation approval date | Date on which the submitted homologation file was approved by Synergrid. - An approval will be granted as soon as Synergrid has a fully compliant homologation dossier. - A homologation only remains valid under the following conditions: - No changes that have an influence on the initial approval are made to (the production of) the units. - There is no new edition of prescription C10/11, or the homologation remains valid under the most recent edition of the prescription C10/11. - The validity date of the test reports in the technical file submitted for approval has not been exceeded. See also the general Synergrid procedure S1/01 for homologation of material, which is applicable.
See also the general Synergrid procedure S1/01 for homologation of material, which is applicable.
Please check ReadMe
before answering

## 3.1 checklist (non-sync)
POWER-GENERATING UNITS TO BE HOMOLOGATED FOR THE LIST C10/26 ACCORDING TO THE REQUIREMENTS OF ANNEX D OF THE TECHNICAL PRESCRIPTION C10/11 ed2.4 (15/10/2025)
3. Checklist according to the requirements of Annex D of Technical Prescriptions C10/11 ed2.4 (15/10/2025)
GLV |  | (brand name) | (series name - one or more series) |  | checklist ed2.4.1 (04/2026)
Instructions for completing this checklist annex D: see at the bottom of the table.
3.1 | CHECKLIST FOR NON-SYNCHRONOUS POWER GENERATING UNITS (mainly inverter-based technologies, such as solar inverters, storage inverters, …)
3.2 | CHECKLIST FOR SYNCHRONOUS POWER GENERATING UNITS (for example gensets, cogenerations, …)
3.3 | CHECKLIST FOR EMERGENCY GROUPS according to C10/11 §2.2.1 (backup power system that only operate in parallel with the distribution network for a short time in the specific sporadic cases)
Reference in annex D of C10/11 ed2.1 dated 01.09.2019 |  | Characteristic | Requirement - black = mandatory - blue = additional information needed in column M | Reference NC RfG | Applicable on what units? |  |  | Required proof of conformity | C10/11 Compliant? | Manufacturer’s reference of proof of conformity | Additional information | Evaluation Synergrid | Explanation Synergrid | Relevant standards for proofs of conformity indicative, non-exhaustive list
[5 empty] | General units other than backup power systems ("emergency groups") according to C10/11 definition §2.2.1 | emergency groups C10/11 §2.2.1 | Specific type B (RfG) |  | completion is considered to be a declaration of honour by manufacturer | available in the technical file: see list of proofs of conformity (sheet 4) | to be filled in by the manufacturer where required (see blue italics) or preferred |  |  | VDE-AR-N 4105: 2018-11 | DIN VDE V 0124-100: 2019-09 | Unit Certificate Req. Listed in (VDE4110:2018-11) | VDE-AR-N 4110:2018-11 | FGW TR 3 Rev 25
(n.a.) | MANDATORY power control system for units suitable for energy storage systems (main text C10/11 §4.1.7 and 7.11.2)
| Power control system using the P1 port of the smart meter of the DSO. Only allowed in "small power generating installations" according to C10/11 §4.1.7. | See C10/11 §4.1.7, §7.11.2 | enter in field "Additional information" : "P1 port". Column G in sheet 2 should also contain this information "P1 port". |  | units suitable for energy storage systems. storage in "small power generating installations" | no |  |  |  |  | (give information)
| Power control system type EnFluRi. Allowed in "small power generating installations" according to C10/11 §4.1.7 and in other installations. | See C10/11 §4.1.7, §7.11.2 | enter in field "Additional information": Name and reference of the provided EnFluRi system. Column G in sheet 2 should also contain this information. |  | units suitable for energy storage systems. storage in "small power generating installations" or other installations | no |  |  |  |  | (give information)
| Power control system other than EnFluRi Only allowed in installations other than "small power generating installations" . | See C10/11 §4.1.7, §7.11.2 | enter in field "Additional information": Name and reference of the provided power control system. Column H in sheet 2 should also contain this information. |  | units suitable for energy storage systems. storage in installations other than "small power generating installations" | no |  |  |  |  | (give information)
D.3 | Integrated automatic separation system (power ≤ 30 kVA)
| Protection functions | Function | Trip setting: settings according to annex C, §C.1 of C10/11
|  | Overvoltage 10 min mean Overvoltage Undervoltage Overfrequency Underfrequency | 230 V + 10% no delay 230 V + 15% no delay 230 V - 20% no delay 51,5 Hz no delay 47,5 Hz no delay |  | units ≤ 30kVA with internal automatic separation system | yes |  | test report | [5 empty] | 6.5.2 | 5.5.7
|  | detection of an island situation (LoM) | method according to EN 50549-1/-2, §4.9.4 (tested according to EN 62116) Enter in field "Additional information": what LoM method according to EN 50549-1/-2, §4.9.4 and what settings? |  | units ≤ 30kVA with internal automatic separation system | yes |  | test report |  |  | (give information) |  |  | 6.5.3 a) | 5.5.10
| ‘Single Fault Tolerance’ | A single fault shall not lead to a loss of the safety functions. | according to EN 50549-1 (2019), §4.13 |  | units ≤ 30kVA with internal automatic separation system | yes |  | test report | [5 empty] | 6.1 | 5.5.2
D.4 | Operating ranges
D.4.1 | Operating frequency range |  |  | Art 13 1
|  | Frequency range | Duration
|  | 47,5 Hz – 49,0 Hz 49,0 Hz – 51,0 Hz 51,0 Hz – 51,5 Hz | 30 minutes Permanent 30 minutes |  | all units | no |  | declaration or test report | [7 empty] | 11.2.3.1 | 10.2.1.2 | 4.7.2
|  | 51,5 Hz – 52,5 Hz | Optional additional frequency range. If available: enter maximum duration in field "Additional information". |  | OPTIONAL for all units | no |  | declaration |  |  | (give information)
D.4.2 | Maximum admissible power reduction in case of underfrequency |  |  | Art 13 4 Art 13 5
| reference ambient conditions | indicate if the capacity is affected by ambient conditions | - fill in "yes / no" in field additional information. - If "yes": also confirm the reference ambient factors at which the capacity was determined, as mentioned in D.4.2. |  | all units | no |  | declaration |  |  | (give information)
D.4.2.1 - Limit for non-synchronous power-generating technology (power park modules)
| limiting curve (see C10/11 figure and table 10) | Parameter | Value
|  | Frequency reduction threshold Maximum reduction rate | 49 Hz 2% /Hz |  | non-synchronous units | no |  | declaration
D.4.3 | Continuous operating voltage range
| Wide (general) operating range: suitable for connection to both LV and HV networks |  | 85% Uref < U < 110% Uref for U < 95% Un reduction of apparent power is allowed |  | all units | yes |  | declaration
| Limited operating range: ONLY suitable for a connection to the HV network (insufficient for connection to LV network) |  | 90% Uc < U < 110% Uc for U < 95% Uc reduction of apparent power is allowed |  | units ONLY suitable for a connection to HV (Limited operating range) | yes |  | declaration or test report | [7 empty] | 11.2.4 | 10.2.1.1 | 4.7.2
D.5 | Immunity to disturbances ("withstand capabilities")
D.5.1 | Immunity to change of frequency (RoCoF) |  |  | Art 13 1.(b)
| Frequency against time profiles for rate of change of frequency immunity |  | C10/11 figure 10: sliding measurement window of 500 ms, max Rocof = 2 Hz/sec |  | all units | no |  | declaration or test report | [7 empty] | 11.2.8 | 10.2.4.3
D.5.2 | Under-voltage ride through (UVRT) (voltage dips) |  |  | Art 14 3.(a) Art 17 3 Art 20 3.(a)
| Basic requirement for units < 1 MW only suitable for installations < 1MW (= type A) |  | Optional conformity with D.5.2. |  | units < 1 MW | no |  | declaration
|  |  | enter the real withstand capability to power dips in the field "Additional information" |  | units < 1 MW | no |  |  |  |  | (give information)
| Mandatory for units ≥ 1 MW (application in installations type B) OPTIONAL for units < 1MW ("type B ready": applicable in installations ≥ 1MW) | non-synchronous generating technology (power park module) | See voltage-time profile in C10/11 figure 12 |  | non-synchronous units ≥ 1 MW OPTIONAL for non-synchronous units < 1MW ("type B ready") | no | X | declaration or test report | [7 empty] | 11.2.5 | 10.2.3 | 4.6.3
|  | Technology where short-circuit power at connection point affects immunity to voltage dips | Enter in field "additional information" the minimum short circuit power to comply with the UVRT requirements. |  | units ≥ 1 MW OPTIONAL for units < 1MW ("type B ready") | no | X | declaration or test report |  |  | (give information) |  |  |  |  | 11.2.5 | 10.2.3
| backup power systems |  | See voltage-time profile in C10/11 figure 13 |  | ONLY for emergency group according to C10/11 §2.2.1 | yes |  | declaration or test report | [6 empty] | 5.9 | 11.2.5 | 10.2.3 | 4.6.3
D.5.3 | Over-voltage ride through (OVRT)
| not applicable in this edition |  | no requirement in this edition
D.6 | Power response to frequency deviations
D.6.1 | Power response to overfrequency |  |  | Art 13 2
| Power response to overfrequency according to EN 50549-1 and 50549-2 §4.6.1 taking into account the additional modifications and information specified in C10/11 D.6.1 |  |  |  | all units | no |  | declaration
| power response to overfrequency | parameter settings | according to C10/11 table 14
|  | Threshold frequency f1 Droop Intentional delay | 50,2 Hz 5% (40% Pref/Hz) 0 s |  | all units | no |  | test report | [5 empty] | 5.7.4.3 | 5.4.4 of 5.4.5 | 11.2.8 | 10.2.4.3 | 4.1.3
|  | optional deactivation threshold fstop | if implemented: deactivated |  | all units | no |  | declaration or test report | [5 empty] | 5.7.4.3 | 5.4.4 of 5.4.5
|  | alternative for droop in NC RfG Art. 13 2.(b) (automatic disconnection and reconnection) | not allowed. Indicate "non applicable" if the alternative is indeed not implemented. | Art. 13 2.(b) | all units | no |  | declaration
| Non-synchronous generating technology | parameter settings | according to C10/11 table 13
| Dynamic step response Settling time (tolerance band +- 10%) | for power increase for power decrease for power increase for power decrease | ≤ 10 seconds for an increase of active power of 50% Pmax ≤ 2 seconds for a reduction of active power of 50% Pmax ≤ 30 seconds for an increase of active power ≤ 20 seconds for a reduction of active power |  | non-synchronous units | no |  | test report | [5 empty] | 5.7.4.3 | 5.4.4 of 5.4.5 | 11.2.8 | 10.2.4.3 | 4.1.3
|  | Dynamic step response for power increase - only for wind generation | ≤ 5 seconds for an increase of active power of 20% Pmax |  | ONLY for non-synchronous units on the basis of WIND energy | no |  | test report | [5 empty] | 5.7.4.3 | 5.4.4 of 5.4.5 | 11.2.8 | 10.2.4.3 | 4.1.3
| restoration active power after deactivation frequency response (f < f1) |  | gradient of 10% Pmax per minute for recovery active power to available power |  | all units | no |  | test report | [5 empty] | 5.7.4.3 | 5.4.4 of 5.4.5 | 11.2.8 | 10.2.4 | 4.1.3
| protection of settings (password, seal, …) |  | Enter in the field "Additional information" which type of seal |  | all units | no |  | declaration |  |  | (give information)
D.6.2 | Power response to underfrequency
| Power response to underfrequency according to EN 50549-1 and 50549-2 §4.6.2 taking into account the additional modifications and information specified in C10/11 D.6.2 |  |  |  | MANDATORY for energy storage systems OPTIONAL for all other units: if activated, must be in accordance with D.6.2 | no |  | declaration
| Dynamic step response and settling time |  | identical to dynamic step response and settling time requirements in D.6.1. |  | energy storage systems OPTIONAL: all other units | no |  | declaration
| power response to underfrequency | parameter settings | according to C10/11 table 15
| Threshold frequency f1 Intentional delay | Threshold frequency f1 Intentional delay | 49,8 Hz 0 s |  | energy storage systems OPTIONAL: all other units | no |  | test report | [5 empty] | 5.7.4.3 | 5.4.6 OF 5.4.7 | 11.2.8 | 10.2.4.3 | 4.1.3
| Droop | Droop for energy storage | 2% (100% Pref/Hz) |  | energy storage systems < 1MW OPTIONAL: all other units |  |  | test report
|  | Droop for power generating unit other than storage | 5% (40% Pref/Hz) |  | OPTIONAL : units other than storage | no |  | test report | [5 empty] | 5.7.4.3 | 5.4.6 OF 5.4.7 | 11.2.8 | 10.2.4.3 | 4.1.3
|  | Droop for storage having a maximum power ≥ 1 MW | 1% (200% Pref/Hz) |  | energy storage systems ≥ 1 MW | no | X | declaration
|  | Droop for storage having a maximum power ≥ 1 MW, incapable of 1% | 2% (100% Pref/Hz) |  | energy storage systems ≥ 1 MW incapable of requirement above | no | X | declaration
|  | storage having a maximum power ≥ 1 MW | if in charging mode during underfrequency, disconnect at treshold within 49Hz-49,2Hz. Enter in the field "Additional information" the implemented treshold. |  | energy storage systems ≥ 1 MW |  | X | declaration |  |  | (give information)
| protection of settings (password, seal, …) |  | Enter in the field "Additional information" which type of seal |  | energy storage systems OPTIONAL: all other units | no |  | declaration |  |  | (give information)
D.7 | Power response to voltage changes
D.7.1 | Voltage support by reactive power |  |  | Art 17 2.(a,b) Art 20 2.(a)
| Voltage support by reactive power according to EN 50549-1 or EN 50549-2 §4.7.2 taking into account the additional modifications and information specified in C10/11 D.7.1 |  |  |  | all units | no |  | declaration
| reactive power range + control modes | small power-generating units - units ≤ 10kVA three-phase - units ≤ 5kVA single-phase See definition in C10/11 §4.1.7. | reactive power range: - U ≤ 105% Un: cos phi = 1 (Q=0) - U >105% Un: free operation with 1≥ cos phi > 0,9 (under-excited). no over-excited operation allowed |  | small power-generating units ONLY to be used in "small power-generating installations" according to C10/11 §4.1.7 | no |  | test report | [5 empty] | 5.7.2.5 | 5.4.8
|  | units ≤ 250kVA | reactive power range as required in EN 50549-1 §4.7.2 (see figure in C10/11 D.7.1) from 0,9 over-excited to 0,9 under-excited) Control modes as required in EN 50549-1 §4.7.2: - set point Q - Q(U) - Cos φ set point - Cos φ (P) |  | units ≤ 250kVA | no |  | test report | [5 empty] | 5.7.2.5 | 5.3.8 | 11.2.4 | 10.2.2.4 | 4.2.2-6
|  | units > 250 kVA OPTIONAL for units ≤ 250kVA | Reactive power range as required in EN 50549-2 §4.7.2 (see figure in C10/11 D.7.1) from -0,33 Q/PD to 0,33 Q/PD Control modes as required in EN 50549-2 §4.7.2: - set point Q - Q(U) - Q(P) - Cos φ set point - Cos φ (P) |  | units > 250kVA OPTIONAL for units ≤ 250kVA | no | X | test report | [5 empty] | 5.7.2.5 | 5.4.8 | 11.2.4 | 10.2.2.4 | 4.2.2-6
|  | EXCEPTION for CHP ≤ 150 kVA | reactive power range: From 0,95 over-excited to 0,95 under-excited |  | ONLY for WKK ≤ 150 kVA | no |  | test report | [5 empty] | 5.7.2.5 | 5.4.8 | 11.2.4 | 10.2.2.4 | 4.2.2-3
|  | EXCEPTION for induction generator ≤ 16A | reactive power range: Operating with active power factor > 0,95 Control modes: none |  | ONLY for induction generators ≤ 16A | no |  | test report | [5 empty] | 5.7.2.5 | 5.4.8 | 11.2.4 | 10.2.2.4 | 4.2.2-3
|  | EXCEPTION for induction generator > 16A | Reactive power range: from ,95 under-excited to 1 Control modes: Only Cos φ set point at PD |  | ONLY for induction generators > 16A | no |  | test report | [5 empty] | 5.7.2.5 | 5.4.8 | 11.2.4 | 10.2.2.4 | 4.2.2-6
|  | EXCEPTION for linear generator | reactive power range: Operating with active power factor > 0,95 Control modes: none |  | ONLY for linear generators | no |  | test report | [5 empty] | 5.7.2.5 | 5.4.8 | 11.2.4 | 10.2.2.4 | 4.2.2-3
|  | EXCEPTION for emergency groups according to C10/11 §2.2.1 | reactive power range: power factor must be as close to 1 and not below the limit of 0,85 in-parallel operation. Control modes: none |  | ONLY for emergency groups according to C10/11 §2.2.1 | yes |  | test report | [5 empty] | 5.7.2.5 | 5.4.8 | 11.2.4 | 10.2.2.4 | 4.2.2-3
| State in field "Additional information" the real technical possibilities of the power-generating unit for the exchange of reactive power. |  |  |  | all units (< 1MW: from 01/05/2020) | no |  |  |  |  | (give information)
| protection of settings (password, seal, …) |  | Enter in the field "Additional information" which type of seal |  | all units (< 1MW: from 01/05/2020) | no |  | declaration |  |  | (give information)
D.7.2 | Voltage related active power reduction P(U)
| OPTIONAL (recommended). If implemented, Mandatory according to EN 50549-1 or EN50549-2 §4.7.3 |  | If implemented, enter in box "additional information" if activated by default or not. |  | OPTIONAL for all units (recommended) | yes |  | declaration |  |  | (give information)
D.7.3 | Provision of additional fast reactive current during faults and voltage steps |  |  | Art. 20 2.(b)
| non-synchronous units < 1 MW |  | Capacity: no requirement. - if capacity not provided: indicate "non applicable" - If capacity is available: standard deactivation, confirm desactivation by indicating "compliant" |  | non-synchronous units < 1 MW | yes |  | declaration or test report | [7 empty] | 11.2.5.5-6 | 10.2.3.2-4 | 4.6.3
| non-synchronous units ≥ 1 MW OPTIONAL for non-synchronous units < 1MW ("type B ready") | maximum power ≥ 1 MW | behaviour according to EN 50549-2 §4.7.4.2.1 + additional information D.7.3 Function deactivated by default. |  | non-synchronous units ≥ 1 MW OPTIONAL for non-synchronous units < 1MW ("type B ready") | yes | X | declaration or test report | [7 empty] | 11.2.5.5-6 | 10.2.3.2-4 | 4.6.3
D.8 | Connection and reconnection |  |  | Art 13 7 Art 14 4
| Connection and reconnection according to EN 50549-1 or EN 50549-2 §4.10 taking into account the additional modifications and information specified in C10/11 D.8 |  | behaviour according to EN 50549-1 or EN 50549-2 §4.10 |  | all units | yes |  | declaration
| Table 16 – conditions for automatic connection and reconnection | Parameter
| Reconnection after tripping of the interface protection relay | Underfrequency Overfrequency Undervoltage Overvoltage Observation time | 49,9 Hz 50,1 Hz 85% Un (LV connection) or 90% Uc (HV connection) 110% Uref 60 s |  | all units | yes |  | test report | [5 empty] | 8.3.1 | 5.6 | 11.2.11 | 10.4.2 | 4.5.2
|  | Maximum active power increase gradient | 10%/min |  | all units | yes |  | test report
|  |  | EXCEPTION: Units that cannot apply the above gradient must provide for an additional delay. |  | EXCEPTION for units not capable of required gradient | yes |  | declaration
| Normal operation starting | Underfrequency Overfrequency (Undervoltage) Overvoltage Observation time Maximum active power increase gradient | 49,9 Hz 50,1 Hz (see next line) 110% Uref 60 s 20%/min |  | all units | yes |  | test report | [5 empty] | 8.3.1 | 5.6 | 11.2.11 | 10.4.1 | 4.5.1
|  | Undervoltage | 85% Uref |  | all units | yes |  | test report
|  |  | EXCEPTION if distinction between connection and reconnection is not possible Undervoltage 90% Uc (HV) |  | EXCEPTION for units technically incapable of distinguishing between coupling and re-coupling | yes |  | test report | [5 empty] | 8.3.1 | 5.6 | 11.2.11 | 10.4.1 | 4.5.1
D.9 | Ceasing production and reduction of active power on set point
D.9.1 | Ceasing production of active power |  |  | Art 13 6
| Ceasing production of active power according to EN 50549-1 AND EN 50549-2 §4.11.1 taking into account the additional modifications and information specified in C10/11 D.9.1 |  |  |  | units > 800W | no |  | declaration
| units ≤ 800 W | no requirement |  |  | units ≤ 800 W ONLY for use in module ≤ 800 W | no |  | declaration
| units > 800 W OPTIONAL for units ≤ 800 W | a logic interface (input port) | stop active power within 5 seconds after receiving an instruction on the input port |  | units > 800W OPTIONAL for units ≤ 800 W | no |  | declaration
|  |  | Principle: contact instead of communication protocol ? Fill in field "additional information". |  | units > 800W OPTIONAL for units ≤ 800 W | no |  | declaration |  |  | (give information)
D.9.2 | Reduction of active power on set point |  |  | Art 14 2
| Reduction of active power on setpoint according to EN 50549-2 §4.11.2 taking into account the additional modifications and information specified in C10/11 D.9.2 |  |  |  | units ≥ 1 MW OPTIONAL for units < 1MW ("type B ready") depending on REGION: also mandatory for unit > 250kVA if required by DSO | no |  | declaration
| units ≥ 1 MW | Reduction of active power on set point | - From maximum power to minimum regulating level with a maximum increment of 10%. - Maximum 0,66% Pn/s and minimum 0,33% Pn/s - Disconnection is allowed if under minimum regulating level. |  | units ≥ 1 MW OPTIONAL for units < 1MW ("type B ready") depending on REGION: also mandatory for unit > 250kVA if required by DSO | no | X | test report | [5 empty] | 5.7.4.1 | 5.4.3 | 11.2.7 | 10.2.4.1 | 4.1.2
| additional equipment for a remote operation of this reduction by DSO |  | Remote service is optional (DSO can request additional equipment for remote control) Indicate "compliant" if remote operation is standard available. |  | units ≥ 1 MW OPTIONAL for units < 1MW ("type B ready") depending on REGION: also mandatory for unit > 250kVA if required by DSO | no | X | declaration
D.10 | Communication – Remote monitoring and control |  |  | Art. 14 5.d
| units ≥ 1 MW |  | necessary functionalities regarding remote monitoring and control to meet the requirements of section 7.13 in C10/11. |  | units ≥ 1 MW OPTIONAL for units < 1MW ("type B ready") depending on REGION: also mandatory for unit > 250kVA if required by DSO | no | X | declaration
EXPLANATIONS FOR COMPLETING THE CHECKLIST IN ANNEX D AND FOR COMPILING THE TECHNICAL FILE | [8 empty] | compliant
non-compliant
Column | Title | Remarks | [6 empty] | non applicable
B - C | Reference in annex D of C10/11 | Reference to the relevant section in the text of C10/11
D | Characteristic | See text C10/11 for a full description.
E | Requirement - black = mandatory - blue = additional information needed in column M | See text C10/11 for a full description.
F | Reference NC RfG | If applicable, the relevant section of the European Network Code Requirements for Generators is provided.
G - H - I | Applicable on what units? | A distinction is made here between the general rule, and specifically the following properties: - requirements to which an exception applies for emergency groups (backup power systems) in accordance with the definition in C10/11 §2.1.1 - requirements specific to installations type B according to the NC RfG, in Belgium these installations are ≥ 1 MW This information is also included in the C10/26 list in tab 2.
J | Required proof of conformity | The following three options are possible:
1. A declaration of honour by the manufacturer regarding conformity with the requirement is sufficient. In this case, the filling in of column K in combination with the signing of the conformity declaration in the first tab applies as the declaration of honour of the manufacturer. There is no need for a separate document for this.
2. A certificate or test report is required. In this case, columns P - Q - R - S - T contain suggestions for relevant sections in relevant standards. See also remark at P - Q - R - S -T (non-exhaustive, indicative list).
The exact requirements of C10/11 can deviate from the international standards: even if a certificate of test report based on an international standard is required, the exact requirement of C10/11 prevails in case it deviates. Therefore, by indicating "compliant" in column K (C10/11 compliant) the manufacturer declares that the power-generating unit is compliant with the requirements of C10/11, including any possible deviations from the references in columns P - Q - R - S - T .
It is allowed to propose certificates or test reports based on other normative references, on the conditions that - the equivalence is proved by the manufacturer; - they are compliant with the conditions for a valid proof of conformity as mentioned below.
3. Either a declaration of honour, or a certificate / test report is required. This choice is given if there is only a suitable normative reference available either for connections on LV (columns P and Q) , or for connections on HV (column R - S - T). A certificate or test report is always preferred if possible or available.
Conditions for a valid proof of conformity: - to be available in Dutch, French, English or German. Other languages are not accepted. - to be available as a separate document in the technical file. Hyperlinks to online documents without the presence of the document itself, or to web pages, are not accepted as valid proof of conformity. - a document with a unique file name (reference), included in the list of proofs of conformity in tab 4, together with an explanation of the content of the document. - additional: conditions for a valid certificate or test report: see tab 1 (declaration of conformity) - Certificates have been drawn up by an EN 45011 (or ISO 17065:2012) certification body accredited for these materials. - Test reports have been drawn up by an ISO 17025:2005 or ISO 17065:2012 laboratory accredited for these tests.
K | C10/11 Compliant? | The filling in of column K in combination with the signing of the declaration of conformity in the first tab applies as the declaration of honour of the manufacturer concerning the conformity of the units with the relevant paragraph in annex D of C10/11.
L | Manufacturer’s reference of proof of conformity | Each piece of evidence used to demonstrate the required conformity shall have a unique reference number, specified in this column. However, the same piece of evidence may be used as evidence for more than one requirement if its contents permit it. Each supporting document mentioned in this column must be completed in the 4th tab "proofs of conformity" together with an explanation, and must be present as a separate document in the technical file. See tab 4 "Proofs of conformity" for the conditions for a valid proof of conformity.
M | Additional information | Here the manufacturer has room for explanations: - mandatory information if indicated in column E - a free explanatory note if the manufacturer feels it necessary.
N | Evaluation Synergrid | This column can be filled in by Synergrid during the study of the homologation application.
O | Explanation Synergrid | This column can be filled in by Synergrid during the study of the homologation application.
P - Q - R - S | Relevant standards for proofs of conformity indicative, non-exhaustive list | For those characteristics for which a certificate or a test report is required, these columns shall indicate the relevant paragraphs of applicable standards. This list is not exhaustive: the manufacturer is free to submit a certificate of conformity via another standard, under the condition that it is compliant with the conditions for a valid proof of conformity, as mentioned above (explanation for column J).
NEW : 3 separate lists "sheet 3":
- 3.1 non-synchronous units
- 3.2 synchronous units
- 3.3 emergency groups

## 3.2 checklist (sync)
POWER-GENERATING UNITS TO BE HOMOLOGATED FOR THE LIST C10/26 ACCORDING TO THE REQUIREMENTS OF ANNEX D OF THE TECHNICAL PRESCRIPTION C10/11 ed2.4 (15/10/2025)
3. Checklist according to the requirements of Annex D of Technical Prescriptions C10/11 ed2.4 (15/10/2025)
GLV |  | (brand name) | (series name - one or more series) |  | checklist ed2.4.1 (04/2026)
Instructions for completing this checklist annex D: see at the bottom of the table.
3.1 | CHECKLIST FOR NON-SYNCHRONOUS POWER GENERATING UNITS (mainly inverter-based technologies, such as solar inverters, storage inverters, …)
3.2 | CHECKLIST FOR SYNCHRONOUS POWER GENERATING UNITS (for example gensets, cogenerations, …)
3.3 | CHECKLIST FOR EMERGENCY GROUPS according to C10/11 §2.2.1 (backup power system that only operate in parallel with the distribution network for a short time in the specific sporadic cases)
Reference in annex D of C10/11 ed2.1 dated 01.09.2019 |  | Characteristic | Requirement - black = mandatory - blue = additional information needed in column M | Reference NC RfG | Applicable on what units? |  |  | Required proof of conformity | C10/11 Compliant? | Manufacturer’s reference of proof of conformity | Additional information | Evaluation Synergrid | Explanation Synergrid | Relevant standards for proofs of conformity indicative, non-exhaustive list
[5 empty] | General units other than backup power systems ("emergency groups") according to C10/11 definition §2.2.1 | emergency groups C10/11 §2.2.1 | Specific type B (RfG) |  | completion is considered to be a declaration of honour by manufacturer | available in the technical file: see list of proofs of conformity (sheet 4) | to be filled in by the manufacturer where required (see blue italics) or preferred |  |  | VDE-AR-N 4105: 2018-11 | DIN VDE V 0124-100: 2019-09 | Unit Certificate Req. Listed in (VDE4110:2018-11) | VDE-AR-N 4110:2018-11 | FGW TR 3 Rev 25
D.3 | Integrated automatic separation system (power ≤ 30 kVA)
| Protection functions | Function | Trip setting: settings according to annex C, §C.1 of C10/11
|  | Overvoltage 10 min mean Overvoltage Undervoltage Overfrequency Underfrequency | 230 V + 10% no delay 230 V + 15% no delay 230 V - 20% no delay 51,5 Hz no delay 47,5 Hz no delay |  | units ≤ 30kVA with internal automatic separation system | yes |  | test report | [5 empty] | 6.5.2 | 5.5.7
|  | detection of an island situation (LoM) | method according to EN 50549-1/-2, §4.9.4 (tested according to EN 62116) Enter in field "Additional information": what LoM method according to EN 50549-1/-2, §4.9.4 and what settings? |  | units ≤ 30kVA with internal automatic separation system | yes |  | test report |  |  | (give information) |  |  | 6.5.3 a) | 5.5.10
| ‘Single Fault Tolerance’ | A single fault shall not lead to a loss of the safety functions. | according to EN 50549-1 (2019), §4.13 |  | units ≤ 30kVA with internal automatic separation system | yes |  | test report | [5 empty] | 6.1 | 5.5.2
D.4 | Operating ranges
D.4.1 | Operating frequency range |  |  | Art 13 1
|  | Frequency range | Duration
|  | 47,5 Hz – 49,0 Hz 49,0 Hz – 51,0 Hz 51,0 Hz – 51,5 Hz | 30 minutes Permanent 30 minutes |  | all units | no |  | declaration or test report | [7 empty] | 11.2.3.1 | 10.2.1.2 | 4.7.2
|  | 51,5 Hz – 52,5 Hz | Optional additional frequency range. If available: enter maximum duration in field "Additional information". |  | OPTIONAL for all units | no |  | declaration |  |  | (give information)
D.4.2 | Maximum admissible power reduction in case of underfrequency |  |  | Art 13 4 Art 13 5
| reference ambient conditions | indicate if the capacity is affected by ambient conditions | - fill in "yes / no" in field additional information. - If "yes": also confirm the reference ambient factors at which the capacity was determined, as mentioned in D.4.2. |  | all units | no |  | declaration |  |  | (give information)
D.4.2.2 - Limits for synchronous power-generating technology
| limiting curve (see C10/11 figure 9 + table 11) | Parameter | Value
| Transient domain (between t1 and t2) | Frequency reduction threshold Maximum reduction rate t1 t2 | 49 Hz 2% /Hz t1≤ 2 seconds t2 30sec |  | synchronous units | no |  | declaration
| Steady state domain (steady state, from t2 onwards) | Frequency reduction threshold Maximum reduction rate t3 | 49,5 Hz 10%/Hz t3≥ 30 minutes |  | synchronous units | no |  | declaration
D.4.3 | Continuous operating voltage range
| Wide (general) operating range: suitable for connection to both LV and HV networks |  | 85% Uref < U < 110% Uref for U < 95% Un reduction of apparent power is allowed |  | all units | yes |  | declaration
| Limited operating range: ONLY suitable for a connection to the HV network (insufficient for connection to LV network) |  | 90% Uc < U < 110% Uc for U < 95% Uc reduction of apparent power is allowed |  | units ONLY suitable for a connection to HV (Limited operating range) | yes |  | declaration or test report | [7 empty] | 11.2.4 | 10.2.1.1 | 4.7.2
D.5 | Immunity to disturbances ("withstand capabilities")
D.5.1 | Immunity to change of frequency (RoCoF) |  |  | Art 13 1.(b)
| Frequency against time profiles for rate of change of frequency immunity |  | C10/11 figure 10: sliding measurement window of 500 ms, max Rocof = 2 Hz/sec |  | all units | no |  | declaration or test report | [7 empty] | 11.2.8 | 10.2.4.3
D.5.2 | Under-voltage ride through (UVRT) (voltage dips) |  |  | Art 14 3.(a) Art 17 3 Art 20 3.(a)
| Basic requirement for units < 1 MW only suitable for installations < 1MW (= type A) |  | Optional conformity with D.5.2. |  | units < 1 MW | no |  | declaration
|  |  | enter the real withstand capability to power dips in the field "Additional information" |  | units < 1 MW | no |  |  |  |  | (give information)
| Mandatory for units ≥ 1 MW (application in installations type B) OPTIONAL for units < 1MW ("type B ready": applicable in installations ≥ 1MW) | synchronous production technologies (more stringent than EN50549) | See voltage-time profile in C10/11 figure 11 |  | synchronous units ≥ 1 MW OPTIONAL for synchronous units < 1MW ("type B ready") | no | X | declaration or test report | [7 empty] | 11.2.5 | 10.2.3 | 4.6.2
|  | Technology where short-circuit power at connection point affects immunity to voltage dips | Enter in field "additional information" the minimum short circuit power to comply with the UVRT requirements. |  | units ≥ 1 MW OPTIONAL for units < 1MW ("type B ready") | no | X | declaration or test report |  |  | (give information) |  |  |  |  | 11.2.5 | 10.2.3
| backup power systems |  | See voltage-time profile in C10/11 figure 13 |  | ONLY for emergency group according to C10/11 §2.2.1 | yes |  | declaration or test report | [6 empty] | 5.9 | 11.2.5 | 10.2.3 | 4.6.3
D.5.3 | Over-voltage ride through (OVRT)
| not applicable in this edition |  | no requirement in this edition
D.6 | Power response to frequency deviations
D.6.1 | Power response to overfrequency |  |  | Art 13 2
| Power response to overfrequency according to EN 50549-1 and 50549-2 §4.6.1 taking into account the additional modifications and information specified in C10/11 D.6.1 |  |  |  | all units | no |  | declaration
| power response to overfrequency | parameter settings | according to C10/11 table 14
|  | Threshold frequency f1 Droop Intentional delay | 50,2 Hz 5% (40% Pref/Hz) 0 s |  | all units | no |  | test report | [5 empty] | 5.7.4.3 | 5.4.4 of 5.4.5 | 11.2.8 | 10.2.4.3 | 4.1.3
|  | optional deactivation threshold fstop | if implemented: deactivated |  | all units | no |  | declaration or test report | [5 empty] | 5.7.4.3 | 5.4.4 of 5.4.5
|  | alternative for droop in NC RfG Art. 13 2.(b) (automatic disconnection and reconnection) | not allowed. Indicate "non applicable" if the alternative is indeed not implemented. | Art. 13 2.(b) | all units | no |  | declaration
| Synchronous generating technology | parameter settings | according to C10/11 table 12
| Dynamic step response Settling time (tolerance band +- 10%) | for power increase for power decrease for power increase for power decrease | ≤ 5 minutes for an increase of active power of 20% Pmax ≤ 8 seconds for a decrease of active power of 45% Pmax ≤ 6 minutes for an increase of active power ≤ 30 seconds for a decrease of active power |  | synchronous units | no |  | test report | [5 empty] | 5.7.4.3 | 5.4.4 of 5.4.5 | 11.2.8 | 10.2.4.3 | 4.1.3
| Alternative power gradient (both with frequency increases and decreases) for gas turbines and internal combustion engines | Pmax < 2 MW | minimum 1,11 % of Pmax per second |  | ONLY for gas turbines and internal combustion engines ≤ 2 MW, incapable of basic requirement | no |  | test report | [5 empty] | 5.7.4.3 | 5.4.4 | 11.2.8 | 10.2.4.3 | 4.1.3
|  | Pmax > 2 MW | minimum 0,33 % of Pmax per second |  | ONLY for gas turbines and internal combustion engines > 2 MW, incapable of basic requirement | no | X | test report | [7 empty] | 11.2.8 | 10.2.4.3 | 4.1.3
| restoration active power after deactivation frequency response (f < f1) |  | gradient of 10% Pmax per minute for recovery active power to available power |  | all units | no |  | test report | [5 empty] | 5.7.4.3 | 5.4.4 of 5.4.5 | 11.2.8 | 10.2.4 | 4.1.3
| protection of settings (password, seal, …) |  | Enter in the field "Additional information" which type of seal |  | all units | no |  | declaration |  |  | (give information)
D.6.2 | Power response to underfrequency
| Power response to underfrequency according to EN 50549-1 and 50549-2 §4.6.2 taking into account the additional modifications and information specified in C10/11 D.6.2 |  |  |  | MANDATORY for energy storage systems OPTIONAL for all other units: if activated, must be in accordance with D.6.2 | no |  | declaration
| Dynamic step response and settling time |  | identical to dynamic step response and settling time requirements in D.6.1. |  | energy storage systems OPTIONAL: all other units | no |  | declaration
| power response to underfrequency | parameter settings | according to C10/11 table 15
| Threshold frequency f1 Intentional delay | Threshold frequency f1 Intentional delay | 49,8 Hz 0 s |  | energy storage systems OPTIONAL: all other units | no |  | test report | [5 empty] | 5.7.4.3 | 5.4.6 OF 5.4.7 | 11.2.8 | 10.2.4.3 | 4.1.3
| Droop | Droop for energy storage | 2% (100% Pref/Hz) |  | energy storage systems < 1MW OPTIONAL: all other units |  |  | test report
|  | Droop for power generating unit other than storage | 5% (40% Pref/Hz) |  | OPTIONAL : units other than storage | no |  | test report | [5 empty] | 5.7.4.3 | 5.4.6 OF 5.4.7 | 11.2.8 | 10.2.4.3 | 4.1.3
|  | Droop for storage having a maximum power ≥ 1 MW | 1% (200% Pref/Hz) |  | energy storage systems ≥ 1 MW | no | X | declaration
|  | Droop for storage having a maximum power ≥ 1 MW, incapable of 1% | 2% (100% Pref/Hz) |  | energy storage systems ≥ 1 MW incapable of requirement above | no | X | declaration
|  | storage having a maximum power ≥ 1 MW | if in charging mode during underfrequency, disconnect at treshold within 49Hz-49,2Hz. Enter in the field "Additional information" the implemented treshold. |  | energy storage systems ≥ 1 MW |  | X | declaration |  |  | (give information)
| protection of settings (password, seal, …) |  | Enter in the field "Additional information" which type of seal |  | energy storage systems OPTIONAL: all other units | no |  | declaration |  |  | (give information)
D.7 | Power response to voltage changes
D.7.1 | Voltage support by reactive power |  |  | Art 17 2.(a,b) Art 20 2.(a)
| Voltage support by reactive power according to EN 50549-1 or EN 50549-2 §4.7.2 taking into account the additional modifications and information specified in C10/11 D.7.1 |  |  |  | all units | no |  | declaration
| reactive power range + control modes | small power-generating units - units ≤ 10kVA three-phase - units ≤ 5kVA single-phase See definition in C10/11 §4.1.7. | reactive power range: - U ≤ 105% Un: cos phi = 1 (Q=0) - U >105% Un: free operation with 1≥ cos phi > 0,9 (under-excited). no over-excited operation allowed |  | small power-generating units ONLY to be used in "small power-generating installations" according to C10/11 §4.1.7 | no |  | test report | [5 empty] | 5.7.2.5 | 5.4.8
|  | units ≤ 250kVA | reactive power range as required in EN 50549-1 §4.7.2 (see figure in C10/11 D.7.1) from 0,9 over-excited to 0,9 under-excited) Control modes as required in EN 50549-1 §4.7.2: - set point Q - Q(U) - Cos φ set point - Cos φ (P) |  | units ≤ 250kVA | no |  | test report | [5 empty] | 5.7.2.5 | 5.3.8 | 11.2.4 | 10.2.2.4 | 4.2.2-6
|  | units > 250 kVA OPTIONAL for units ≤ 250kVA | Reactive power range as required in EN 50549-2 §4.7.2 (see figure in C10/11 D.7.1) from -0,33 Q/PD to 0,33 Q/PD Control modes as required in EN 50549-2 §4.7.2: - set point Q - Q(U) - Q(P) - Cos φ set point - Cos φ (P) |  | units > 250kVA OPTIONAL for units ≤ 250kVA | no | X | test report | [5 empty] | 5.7.2.5 | 5.4.8 | 11.2.4 | 10.2.2.4 | 4.2.2-6
|  | additional requirement for synchronous units ≥ 1 MW (application in installations type B) OPTIONAL for units < 1MW ("type B ready": applicable in installations ≥ 1MW) | Control modes: - mandatory alternative for Q(U): equipment with a permanent automatic excitation control system (see text C10/11). - Setpoint: selectable in the continuous operating domain for the voltage (D.4.3). (selection of setpoint by DSO) Equipment must be expandable to allow remote selection of set point |  | synchronous units ≥ 1 MW OPTIONAL for synchronous units < 1MW ("type B ready") | no | X | test report | [5 empty] | 5.7.2.5 | 5.4.8 | 11.2.4 | 10.2.2.4 | 4.2.2-6
|  | EXCEPTION for CHP ≤ 150 kVA | reactive power range: From 0,95 over-excited to 0,95 under-excited |  | ONLY for WKK ≤ 150 kVA | no |  | test report | [5 empty] | 5.7.2.5 | 5.4.8 | 11.2.4 | 10.2.2.4 | 4.2.2-3
|  | EXCEPTION for induction generator ≤ 16A | reactive power range: Operating with active power factor > 0,95 Control modes: none |  | ONLY for induction generators ≤ 16A | no |  | test report | [5 empty] | 5.7.2.5 | 5.4.8 | 11.2.4 | 10.2.2.4 | 4.2.2-3
|  | EXCEPTION for induction generator > 16A | Reactive power range: from ,95 under-excited to 1 Control modes: Only Cos φ set point at PD |  | ONLY for induction generators > 16A | no |  | test report | [5 empty] | 5.7.2.5 | 5.4.8 | 11.2.4 | 10.2.2.4 | 4.2.2-6
|  | EXCEPTION for linear generator | reactive power range: Operating with active power factor > 0,95 Control modes: none |  | ONLY for linear generators | no |  | test report | [5 empty] | 5.7.2.5 | 5.4.8 | 11.2.4 | 10.2.2.4 | 4.2.2-3
|  | EXCEPTION for emergency groups according to C10/11 §2.2.1 | reactive power range: power factor must be as close to 1 and not below the limit of 0,85 in-parallel operation. Control modes: none |  | ONLY for emergency groups according to C10/11 §2.2.1 | yes |  | test report | [5 empty] | 5.7.2.5 | 5.4.8 | 11.2.4 | 10.2.2.4 | 4.2.2-3
| State in field "Additional information" the real technical possibilities of the power-generating unit for the exchange of reactive power. |  |  |  | all units (< 1MW: from 01/05/2020) | no |  |  |  |  | (give information)
| protection of settings (password, seal, …) |  | Enter in the field "Additional information" which type of seal |  | all units (< 1MW: from 01/05/2020) | no |  | declaration |  |  | (give information)
D.7.2 | Voltage related active power reduction P(U)
| OPTIONAL (recommended). If implemented, Mandatory according to EN 50549-1 or EN50549-2 §4.7.3 |  | If implemented, enter in box "additional information" if activated by default or not. |  | OPTIONAL for all units (recommended) | yes |  | declaration |  |  | (give information)
D.8 | Connection and reconnection |  |  | Art 13 7 Art 14 4
| Connection and reconnection according to EN 50549-1 or EN 50549-2 §4.10 taking into account the additional modifications and information specified in C10/11 D.8 |  | behaviour according to EN 50549-1 or EN 50549-2 §4.10 |  | all units | yes |  | declaration
| Table 16 – conditions for automatic connection and reconnection | Parameter
| Reconnection after tripping of the interface protection relay | Underfrequency Overfrequency Undervoltage Overvoltage Observation time | 49,9 Hz 50,1 Hz 85% Un (LV connection) or 90% Uc (HV connection) 110% Uref 60 s |  | all units | yes |  | test report | [5 empty] | 8.3.1 | 5.6 | 11.2.11 | 10.4.2 | 4.5.2
|  | Maximum active power increase gradient | 10%/min |  | all units | yes |  | test report
|  |  | EXCEPTION: Units that cannot apply the above gradient must provide for an additional delay. |  | EXCEPTION for units not capable of required gradient | yes |  | declaration
| Normal operation starting | Underfrequency Overfrequency (Undervoltage) Overvoltage Observation time Maximum active power increase gradient | 49,9 Hz 50,1 Hz (see next line) 110% Uref 60 s 20%/min |  | all units | yes |  | test report | [5 empty] | 8.3.1 | 5.6 | 11.2.11 | 10.4.1 | 4.5.1
|  | Undervoltage | 85% Uref |  | all units | yes |  | test report
|  |  | EXCEPTION if distinction between connection and reconnection is not possible Undervoltage 90% Uc (HV) |  | EXCEPTION for units technically incapable of distinguishing between coupling and re-coupling | yes |  | test report | [5 empty] | 8.3.1 | 5.6 | 11.2.11 | 10.4.1 | 4.5.1
D.9 | Ceasing production and reduction of active power on set point
D.9.1 | Ceasing production of active power |  |  | Art 13 6
| Ceasing production of active power according to EN 50549-1 AND EN 50549-2 §4.11.1 taking into account the additional modifications and information specified in C10/11 D.9.1 |  |  |  | units > 800W | no |  | declaration
| units ≤ 800 W | no requirement |  |  | units ≤ 800 W ONLY for use in module ≤ 800 W | no |  | declaration
| units > 800 W OPTIONAL for units ≤ 800 W | a logic interface (input port) | stop active power within 5 seconds after receiving an instruction on the input port |  | units > 800W OPTIONAL for units ≤ 800 W | no |  | declaration
|  |  | Principle: contact instead of communication protocol ? Fill in field "additional information". |  | units > 800W OPTIONAL for units ≤ 800 W | no |  | declaration |  |  | (give information)
D.9.2 | Reduction of active power on set point |  |  | Art 14 2
| Reduction of active power on setpoint according to EN 50549-2 §4.11.2 taking into account the additional modifications and information specified in C10/11 D.9.2 |  |  |  | units ≥ 1 MW OPTIONAL for units < 1MW ("type B ready") depending on REGION: also mandatory for unit > 250kVA if required by DSO | no |  | declaration
| units ≥ 1 MW | Reduction of active power on set point | - From maximum power to minimum regulating level with a maximum increment of 10%. - Maximum 0,66% Pn/s and minimum 0,33% Pn/s - Disconnection is allowed if under minimum regulating level. |  | units ≥ 1 MW OPTIONAL for units < 1MW ("type B ready") depending on REGION: also mandatory for unit > 250kVA if required by DSO | no | X | test report | [5 empty] | 5.7.4.1 | 5.4.3 | 11.2.7 | 10.2.4.1 | 4.1.2
| additional equipment for a remote operation of this reduction by DSO |  | Remote service is optional (DSO can request additional equipment for remote control) Indicate "compliant" if remote operation is standard available. |  | units ≥ 1 MW OPTIONAL for units < 1MW ("type B ready") depending on REGION: also mandatory for unit > 250kVA if required by DSO | no | X | declaration
D.10 | Communication – Remote monitoring and control |  |  | Art. 14 5.d
| units ≥ 1 MW |  | necessary functionalities regarding remote monitoring and control to meet the requirements of section 7.13 in C10/11. |  | units ≥ 1 MW OPTIONAL for units < 1MW ("type B ready") depending on REGION: also mandatory for unit > 250kVA if required by DSO | no | X | declaration
EXPLANATIONS FOR COMPLETING THE CHECKLIST IN ANNEX D AND FOR COMPILING THE TECHNICAL FILE | [8 empty] | compliant
non-compliant
Column | Title | Remarks | [6 empty] | non applicable
B - C | Reference in annex D of C10/11 | Reference to the relevant section in the text of C10/11
D | Characteristic | See text C10/11 for a full description.
E | Requirement - black = mandatory - blue = additional information needed in column M | See text C10/11 for a full description.
F | Reference NC RfG | If applicable, the relevant section of the European Network Code Requirements for Generators is provided.
G - H - I | Applicable on what units? | A distinction is made here between the general rule, and specifically the following properties: - requirements to which an exception applies for emergency groups (backup power systems) in accordance with the definition in C10/11 §2.1.1 - requirements specific to installations type B according to the NC RfG, in Belgium these installations are ≥ 1 MW This information is also included in the C10/26 list in tab 2.
J | Required proof of conformity | The following three options are possible:
1. A declaration of honour by the manufacturer regarding conformity with the requirement is sufficient. In this case, the filling in of column K in combination with the signing of the conformity declaration in the first tab applies as the declaration of honour of the manufacturer. There is no need for a separate document for this.
2. A certificate or test report is required. In this case, columns P - Q - R - S - T contain suggestions for relevant sections in relevant standards. See also remark at P - Q - R - S -T (non-exhaustive, indicative list).
The exact requirements of C10/11 can deviate from the international standards: even if a certificate of test report based on an international standard is required, the exact requirement of C10/11 prevails in case it deviates. Therefore, by indicating "compliant" in column K (C10/11 compliant) the manufacturer declares that the power-generating unit is compliant with the requirements of C10/11, including any possible deviations from the references in columns P - Q - R - S - T .
It is allowed to propose certificates or test reports based on other normative references, on the conditions that - the equivalence is proved by the manufacturer; - they are compliant with the conditions for a valid proof of conformity as mentioned below.
3. Either a declaration of honour, or a certificate / test report is required. This choice is given if there is only a suitable normative reference available either for connections on LV (columns P and Q) , or for connections on HV (column R - S - T). A certificate or test report is always preferred if possible or available.
Conditions for a valid proof of conformity: - to be available in Dutch, French, English or German. Other languages are not accepted. - to be available as a separate document in the technical file. Hyperlinks to online documents without the presence of the document itself, or to web pages, are not accepted as valid proof of conformity. - a document with a unique file name (reference), included in the list of proofs of conformity in tab 4, together with an explanation of the content of the document. - additional: conditions for a valid certificate or test report: see tab 1 (declaration of conformity) - Certificates have been drawn up by an EN 45011 (or ISO 17065:2012) certification body accredited for these materials. - Test reports have been drawn up by an ISO 17025:2005 or ISO 17065:2012 laboratory accredited for these tests.
K | C10/11 Compliant? | The filling in of column K in combination with the signing of the declaration of conformity in the first tab applies as the declaration of honour of the manufacturer concerning the conformity of the units with the relevant paragraph in annex D of C10/11.
L | Manufacturer’s reference of proof of conformity | Each piece of evidence used to demonstrate the required conformity shall have a unique reference number, specified in this column. However, the same piece of evidence may be used as evidence for more than one requirement if its contents permit it. Each supporting document mentioned in this column must be completed in the 4th tab "proofs of conformity" together with an explanation, and must be present as a separate document in the technical file. See tab 4 "Proofs of conformity" for the conditions for a valid proof of conformity.
M | Additional information | Here the manufacturer has room for explanations: - mandatory information if indicated in column E - a free explanatory note if the manufacturer feels it necessary.
N | Evaluation Synergrid | This column can be filled in by Synergrid during the study of the homologation application.
O | Explanation Synergrid | This column can be filled in by Synergrid during the study of the homologation application.
P - Q - R - S | Relevant standards for proofs of conformity indicative, non-exhaustive list | For those characteristics for which a certificate or a test report is required, these columns shall indicate the relevant paragraphs of applicable standards. This list is not exhaustive: the manufacturer is free to submit a certificate of conformity via another standard, under the condition that it is compliant with the conditions for a valid proof of conformity, as mentioned above (explanation for column J).
NEW : 3 separate lists "sheet 3":
- 3.1 non-synchronous units
- 3.2 synchronous units
- 3.3 emergency groups

## 3.3 checklist (emergency)
POWER-GENERATING UNITS TO BE HOMOLOGATED FOR THE LIST C10/26 ACCORDING TO THE REQUIREMENTS OF ANNEX D OF THE TECHNICAL PRESCRIPTION C10/11 ed2.4 (15/10/2025)
3. Checklist according to the requirements of Annex D of Technical Prescriptions C10/11 ed2.4 (15/10/2025)
GLV |  | (brand name) | (series name - one or more series) |  | checklist ed2.4.1 (04/2026)
Instructions for completing this checklist annex D: see at the bottom of the table.
3.1 | CHECKLIST FOR NON-SYNCHRONOUS POWER GENERATING UNITS (mainly inverter-based technologies, such as solar inverters, storage inverters, …)
3.2 | CHECKLIST FOR SYNCHRONOUS POWER GENERATING UNITS (for example gensets, cogenerations, …)
3.3 | CHECKLIST FOR EMERGENCY GROUPS according to C10/11 §2.2.1 (backup power system that only operate in parallel with the distribution network for a short time in the specific sporadic cases)
Reference in annex D of C10/11 ed2.1 dated 01.09.2019 |  | Characteristic | Requirement - black = mandatory - blue = additional information needed in column M | Reference NC RfG | Applicable on what units? |  |  | Required proof of conformity | C10/11 Compliant? | Manufacturer’s reference of proof of conformity | Additional information | Evaluation Synergrid | Explanation Synergrid | Relevant standards for proofs of conformity indicative, non-exhaustive list
[5 empty] | General units other than backup power systems ("emergency groups") according to C10/11 definition §2.2.1 | emergency groups C10/11 §2.2.1 | Specific type B (RfG) |  | completion is considered to be a declaration of honour by manufacturer | available in the technical file: see list of proofs of conformity (sheet 4) | to be filled in by the manufacturer where required (see blue italics) or preferred |  |  | VDE-AR-N 4105: 2018-11 | DIN VDE V 0124-100: 2019-09 | Unit Certificate Req. Listed in (VDE4110:2018-11) | VDE-AR-N 4110:2018-11 | FGW TR 3 Rev 25
D.3 | Integrated automatic separation system (power ≤ 30 kVA)
| Protection functions | Function | Trip setting: settings according to annex C, §C.1 of C10/11
|  | Overvoltage 10 min mean Overvoltage Undervoltage Overfrequency Underfrequency | 230 V + 10% no delay 230 V + 15% no delay 230 V - 20% no delay 51,5 Hz no delay 47,5 Hz no delay |  | units ≤ 30kVA with internal automatic separation system | yes |  | test report | [5 empty] | 6.5.2 | 5.5.7
|  | detection of an island situation (LoM) | method according to EN 50549-1/-2, §4.9.4 (tested according to EN 62116) Enter in field "Additional information": what LoM method according to EN 50549-1/-2, §4.9.4 and what settings? |  | units ≤ 30kVA with internal automatic separation system | yes |  | test report |  |  | (give information) |  |  | 6.5.3 a) | 5.5.10
| ‘Single Fault Tolerance’ | A single fault shall not lead to a loss of the safety functions. | according to EN 50549-1 (2019), §4.13 |  | units ≤ 30kVA with internal automatic separation system | yes |  | test report | [5 empty] | 6.1 | 5.5.2
D.4 | Operating ranges
D.4.3 | Continuous operating voltage range
| Wide (general) operating range: suitable for connection to both LV and HV networks |  | 85% Uref < U < 110% Uref for U < 95% Un reduction of apparent power is allowed |  | all units | yes |  | declaration
| Limited operating range: ONLY suitable for a connection to the HV network (insufficient for connection to LV network) |  | 90% Uc < U < 110% Uc for U < 95% Uc reduction of apparent power is allowed |  | units ONLY suitable for a connection to HV (Limited operating range) | yes |  | declaration or test report | [7 empty] | 11.2.4 | 10.2.1.1 | 4.7.2
D.5 | Immunity to disturbances ("withstand capabilities")
D.5.2 | Under-voltage ride through (UVRT) (voltage dips) |  |  | Art 14 3.(a) Art 17 3 Art 20 3.(a)
| backup power systems |  | See voltage-time profile in C10/11 figure 13 |  | ONLY for emergency group according to C10/11 §2.2.1 | yes |  | declaration or test report | [6 empty] | 5.9 | 11.2.5 | 10.2.3 | 4.6.3
D.7 | Power response to voltage changes
D.7.1 | Voltage support by reactive power |  |  | Art 17 2.(a,b) Art 20 2.(a)
| EXCEPTION for emergency groups according to C10/11 §2.2.1 |  | reactive power range: power factor must be as close to 1 and not below the limit of 0,85 in-parallel operation. Control modes: none |  | ONLY for emergency groups according to C10/11 §2.2.1 | yes |  | declaration or test report | [5 empty] | 5.7.2.5 | 5.4.8 | 11.2.4 | 10.2.2.4 | 4.2.2-3
D.7.2 | Voltage related active power reduction P(U)
| OPTIONAL (recommended). If implemented, Mandatory according to EN 50549-1 or EN50549-2 §4.7.3 |  | If implemented, enter in box "additional information" if activated by default or not. |  | OPTIONAL for all units (recommended) | yes |  | declaration |  |  | (give information)
D.7.3 | Provision of additional fast reactive current during faults and voltage steps |  |  | Art. 20 2.(b)
| non-synchronous units < 1 MW |  | Capacity: no requirement. - if capacity not provided: indicate "non applicable" - If capacity is available: standard deactivation, confirm desactivation by indicating "compliant" |  | non-synchronous units < 1 MW | yes |  | declaration or test report | [7 empty] | 11.2.5.5-6 | 10.2.3.2-4 | 4.6.3
| non-synchronous units ≥ 1 MW OPTIONAL for non-synchronous units < 1MW ("type B ready") | maximum power ≥ 1 MW | behaviour according to EN 50549-2 §4.7.4.2.1 + additional information D.7.3 Function deactivated by default. |  | non-synchronous units ≥ 1 MW OPTIONAL for non-synchronous units < 1MW ("type B ready") | yes | X | declaration or test report | [7 empty] | 11.2.5.5-6 | 10.2.3.2-4 | 4.6.3
D.8 | Connection and reconnection |  |  | Art 13 7 Art 14 4
| Connection and reconnection according to EN 50549-1 or EN 50549-2 §4.10 taking into account the additional modifications and information specified in C10/11 D.8 |  | behaviour according to EN 50549-1 or EN 50549-2 §4.10 |  | all units | yes |  | declaration
| Table 16 – conditions for automatic connection and reconnection | Parameter
| Reconnection after tripping of the interface protection relay | Underfrequency Overfrequency Undervoltage Overvoltage Observation time | 49,9 Hz 50,1 Hz 85% Un (LV connection) or 90% Uc (HV connection) 110% Uref 60 s |  | all units | yes |  | test report | [5 empty] | 8.3.1 | 5.6 | 11.2.11 | 10.4.2 | 4.5.2
|  | Maximum active power increase gradient | 10%/min |  | all units | yes |  | test report
|  |  | EXCEPTION: Units that cannot apply the above gradient must provide for an additional delay. |  | EXCEPTION for units not capable of required gradient | yes |  | declaration
| Normal operation starting | Underfrequency Overfrequency (Undervoltage) Overvoltage Observation time Maximum active power increase gradient | 49,9 Hz 50,1 Hz (see next line) 110% Uref 60 s 20%/min |  | all units | yes |  | test report | [5 empty] | 8.3.1 | 5.6 | 11.2.11 | 10.4.1 | 4.5.1
|  | Undervoltage | 85% Uref |  | all units | yes |  | test report
|  |  | EXCEPTION if distinction between connection and reconnection is not possible Undervoltage 90% Uc (HV) |  | EXCEPTION for units technically incapable of distinguishing between coupling and re-coupling | yes |  | test report | [5 empty] | 8.3.1 | 5.6 | 11.2.11 | 10.4.1 | 4.5.1
EXPLANATIONS FOR COMPLETING THE CHECKLIST IN ANNEX D AND FOR COMPILING THE TECHNICAL FILE | [8 empty] | compliant
non-compliant
Column | Title | Remarks | [6 empty] | non applicable
B - C | Reference in annex D of C10/11 | Reference to the relevant section in the text of C10/11
D | Characteristic | See text C10/11 for a full description.
E | Requirement - black = mandatory - blue = additional information needed in column M | See text C10/11 for a full description.
F | Reference NC RfG | If applicable, the relevant section of the European Network Code Requirements for Generators is provided.
G - H - I | Applicable on what units? | A distinction is made here between the general rule, and specifically the following properties: - requirements to which an exception applies for emergency groups (backup power systems) in accordance with the definition in C10/11 §2.1.1 - requirements specific to installations type B according to the NC RfG, in Belgium these installations are ≥ 1 MW This information is also included in the C10/26 list in tab 2.
J | Required proof of conformity | The following three options are possible:
1. A declaration of honour by the manufacturer regarding conformity with the requirement is sufficient. In this case, the filling in of column K in combination with the signing of the conformity declaration in the first tab applies as the declaration of honour of the manufacturer. There is no need for a separate document for this.
2. A certificate or test report is required. In this case, columns P - Q - R - S - T contain suggestions for relevant sections in relevant standards. See also remark at P - Q - R - S -T (non-exhaustive, indicative list).
The exact requirements of C10/11 can deviate from the international standards: even if a certificate of test report based on an international standard is required, the exact requirement of C10/11 prevails in case it deviates. Therefore, by indicating "compliant" in column K (C10/11 compliant) the manufacturer declares that the power-generating unit is compliant with the requirements of C10/11, including any possible deviations from the references in columns P - Q - R - S - T .
It is allowed to propose certificates or test reports based on other normative references, on the conditions that - the equivalence is proved by the manufacturer; - they are compliant with the conditions for a valid proof of conformity as mentioned below.
3. Either a declaration of honour, or a certificate / test report is required. This choice is given if there is only a suitable normative reference available either for connections on LV (columns P and Q) , or for connections on HV (column R - S - T). A certificate or test report is always preferred if possible or available.
Conditions for a valid proof of conformity: - to be available in Dutch, French, English or German. Other languages are not accepted. - to be available as a separate document in the technical file. Hyperlinks to online documents without the presence of the document itself, or to web pages, are not accepted as valid proof of conformity. - a document with a unique file name (reference), included in the list of proofs of conformity in tab 4, together with an explanation of the content of the document. - additional: conditions for a valid certificate or test report: see tab 1 (declaration of conformity) - Certificates have been drawn up by an EN 45011 (or ISO 17065:2012) certification body accredited for these materials. - Test reports have been drawn up by an ISO 17025:2005 or ISO 17065:2012 laboratory accredited for these tests.
K | C10/11 Compliant? | The filling in of column K in combination with the signing of the declaration of conformity in the first tab applies as the declaration of honour of the manufacturer concerning the conformity of the units with the relevant paragraph in annex D of C10/11.
L | Manufacturer’s reference of proof of conformity | Each piece of evidence used to demonstrate the required conformity shall have a unique reference number, specified in this column. However, the same piece of evidence may be used as evidence for more than one requirement if its contents permit it. Each supporting document mentioned in this column must be completed in the 4th tab "proofs of conformity" together with an explanation, and must be present as a separate document in the technical file. See tab 4 "Proofs of conformity" for the conditions for a valid proof of conformity.
M | Additional information | Here the manufacturer has room for explanations: - mandatory information if indicated in column E - a free explanatory note if the manufacturer feels it necessary.
N | Evaluation Synergrid | This column can be filled in by Synergrid during the study of the homologation application.
O | Explanation Synergrid | This column can be filled in by Synergrid during the study of the homologation application.
P - Q - R - S | Relevant standards for proofs of conformity indicative, non-exhaustive list | For those characteristics for which a certificate or a test report is required, these columns shall indicate the relevant paragraphs of applicable standards. This list is not exhaustive: the manufacturer is free to submit a certificate of conformity via another standard, under the condition that it is compliant with the conditions for a valid proof of conformity, as mentioned above (explanation for column J).
NEW : 3 separate lists "sheet 3":
- 3.1 non-synchronous units
- 3.2 synchronous units
- 3.3 emergency groups