## 1 GLV
GLV |  | (brand name) | (series name - one or more series)
C2/115 - DECLARATION OF CONFORMITY for prefabricated enclosures C2/115-3.2 ed4 (06/2025)
for homologation for the list C2/115-0 according to the requirements of the technical specification C2/115-3.2 ed1 - 05/2025
The undersigned, |  | Manufacturer: |  | Represented by:
|  | Address: |  | Country:
email:
Telephone:
Hereby declares that each enclosure listed in the tab 'list of prefabricated enclosures' of this homologation application complies with the following conditions:
1. The enclosures comply with the the requirements of the Synergrid technical specification C2/115-3 ed3.0 (12/2021)
2. In order to substantiate this, a technical file has been submitted for all enclosures listed in sheet 2 'C2/115-0 list of prefabricated enclosures' of this homologation application. The technical file was drawn up based on sheet 3 "checklist C2/115-3" of this file, duly and correctly completed by the manufacturer, accompanied by all the required proof of conformity.
2.1 For technical requirements for which the required proof of conformity (column H in checklist C2/115-3) is a declaration of honour by the manufacturer, the manufacturer declares by signing and dating this declaration of conformity the correctness of the information (compliant / non-compliant / not applicable) provided by him or her in columns I and J of this checklist.
2.2. For technical requirements for which the required proof of conformity (column H in checklist C2/115-3) is a test report or a certificate, the necessary test reports and/or certificates are available * in the technical file. Type test reports comply to the requirements in §7.1 of C2/115-3.
2.3 A numbered list of all document references (test reports, certificates, data sheets, drawings/plans, instructions, …) necessary to prove conformity, and mentioned as proof in column J of sheet 3, is available in sheet 4 of this technical file.
Done at: |  | (location) |  | Homologated by Synergrid on:
On: |  | (date) |  | Stamp Synergrid & signature:
Stamp manufacturer & signature
* See procedure C2/115-1, §2.2.
COLOR LEGEND
Mandatory field to be filled in
text | Mandatory field to be filled in
Voluntary field to be filled in
Reserved for Synergrid
text | Title
text | Title
text | Informative text field
text | Information for the applicant
Empty field; no action required

## 2 list prefabricated enclosures
PREFABRICATED ENCLOSURES TO BE HOMOLOGATED FOR LIST C2/115-0 ACCORDING TO THE REQUIREMENTS OF THE TECHNICAL SPECIFICATION C2/115-3.2 ed1 (05/2025)
2. C2/115-0 list of prefabricated enclosures for which homologation is requested
GLV | (brand name) | (series name)
Checklist ed1 (06/2025)
For an explanation of the used colour code: see tab GLV
1 | 2 | 3 | 4 | 5 |  |  | 6 |  | 7 | 8 | 9 | 10 | 11 | 12 |  |  |  |  | 13
SYNERGRID reference number (GLVxxx-yy-zzzz) | BRAND NAME (Manufacturer) | Name of the product SERIES | NAME or REFERENCE of the model of the enclosure | Dimensions of the enclosure: L x D x H (m) external dimensions |  |  | TYPE |  | Net volume of the enclosure (m³) internal net volume without equipment installed | Maximum load of the floor slab (kg/m²) | Homologated for material class AAxx | Homologated for global earthing or non global earthing or both | Number of ventilation grids in the enclosure | Suitable transformer(s) |  |  |  |  | Synergrid approval
Date of homologation
|  |  |  | Length (m) | Depht (m) | Height (m) | Walk-in enclosure | Non-walk-in enclosure | [5 empty] | Maximum number of transformers | Maximum rated power (kVA) of each transformer | Load factor (%) of each transformer | Maximum rated weight (kg) of each transformer | Maximum total losses (W) of each transformer
[14 empty] | - | - | - | - | -
[14 empty] | - | - | - | - | -
[14 empty] | - | - | - | - | -
[14 empty] | - | - | - | - | -
[14 empty] | - | - | - | - | -
[14 empty] | - | - | - | - | -
[14 empty] | - | - | - | - | -
[14 empty] | - | - | - | - | -
[14 empty] | - | - | - | - | -
[14 empty] | - | - | - | - | -
[14 empty] | - | - | - | - | -
[14 empty] | - | - | - | - | -
[14 empty] | - | - | - | - | -
EXPLANATIONS FOR THE COMPLETION OF THE TABLE
Column | Title | Remarks
1 | SYNERGRID reference number (GLVxxx-yy-zzzz) | In the case of a positive homologation, each homologated enclosure is given a unique Synergrid reference number: xxx = unique reference or the manufacturer yy = serial number of manufacturer homologation request (for example: for the first homologation request, yy = 01) zzzz = unique unit reference for the manufacturer xxx (for example, for the first enclosure in the list, zzzz=0001) Note : "GLV" is the internal Synergrid-abbreviation for Declaration of Conformity, based on the Dutch word "Gelijkvormigheidsverklaring".
2 | Brand name | Brand name under which the unit is marketed by the manufacturer on the Belgian market
3 | Name of the product series | Name of the product series. Note: For each separate product range (or each group of enclosures with common characteristics) a separate checklist according to sheet 3 "checklist C2/115-3) is required.
4 | NAME or REFERENCE of the model of the enclosure | Unique product name or reference. Units of the same product series must be unequivocally distinguished from each other through this name or reference. Each line of the above list corresponds with one unique enclosure.
5 | Dimensions of the enclosure: L x D x H (m) | External dimensions (m) of the enclosure. Whatever has the greatest width and depth should be filled in (the switch room or the basement).The height is the total height from ground level to the top of the roof.
6 | Type of enclosure | Indicate with a "X" if the enclosure is a walk-in or non-walk-in type of enclosure
7 | Volume of the enclosure (m³) | Net internal volume of the enclosure without equipment (maximum volume available for gas expansion and cooling).
8 | Maximum load of the floor slab (kg/m²) | Maximum (mobile) load of the floor slab: to take into consideration based on the material planned to be placed inside.
9 | Homologated for material class Aaxx | Classes of HV-switchgear according to C2/113-0 for which this enclosure is homologated
10 | Homologated for global earthing or non global earthing or both | Enclosure only suitable for global earthing, or for non-global earthing or for the both of them.
11 | Number of ventilation grids in the enclosure | Number of ventilation grids foreseen in the enclosure.
12 | Suitable transformer(s) | Characteristics of the suitable transformer(s) for which the enclosure is designed and homologated: - Maximum number of transformers (with characteristics compliant to the next 3 columns) that can be installed in the enclosure - Homologated for a transformer with indicated maximum power. See also §5.4.1 of C2/115-3 - Homologated for a transformer with indicated load factor (%), this is relevant in case the permanent load factor is lower than 100%. See also §8.1 of C2/115-3 (lowest load factor must be mentionned) - Homologated for a transformer with indicated maximum weight. See also §5.4.1 of C2/115-3 - Homologated for a transformer with indicated maximum total losses. See also §5.4.1 of C2/115-3.For these losses, reference can also be made to the losses as presented in the European guideline for Eco-design of transformers (Tier 1 or, Tier 2)
13 | Synergrid approval date of homologation | Date on which the submitted homologation file was approved by Synergrid. A homologation only remains valid under the following conditions: - There is less than 7 years time difference between the current date and the homologation date. - No changes that have an influence on the initial homologation approval are made to (the production of) the units. - There is no new edition of the specification C2/115-3, the underlying technical prescription C2/112, or the relevant standards. - The validity date of the test reports in the technical file submitted for homologation has not been exceeded. See also the general Synergrid procedure S1/01 for homologation of material, which is applicable. (1)
(1) - S1/01 Technical specification: procedure for application for homologation and renewal of homologation of materials

## 3 checklist C2-115-3
PREFABRICATED ENCLOSURES TO BE HOMOLOGATED FOR LIST C2/115-0 ACCORDING TO THE REQUIREMENTS OF THE TECHNICAL SPECIFICATION C2/115-3.2 ed1 (05/2025)
3. Conformity assessment guide (checklist) according to the requirements of technical specification C2/115-3.2
GLV |  |  | (brand name) | (series name - one or more series)
Instructions for completing this conformity assessment guide C2/115-3 (checklist): see at the bottom of the table.
For an explanation of the used colour code: see tab GLV of at the botom of this page
Reference in C2/115-3 ed1.0 dated 01.04.2021 |  |  | Characteristic | Requirement | Normative reference | Required proof of conformity | C2/115-3 Compliant? | Manufacturer’s reference of proof of conformity and/or additional information | Evaluation Synergrid | Explanation Synergrid
[7 empty] | Completion is considered to be a declaration of honour by manufacturer | Reference must be available in the technical file: see list of proofs of conformity (sheet 4) Additional information to be filled in where required of preferred.
1 |  | Object
|  | Type of enclosure | Non-walk-in enclosure? |  |  | (indicate compliant or non-applicable in column I)
4 |  | Normal and specific service conditions
|  | Service conditions |  | The enclosure complies with all requirements in §4 | NBN EN 62271-1 IEC TS 60815-1:2008 |  |  | If any deviations, specify information
5 |  | Rated characteristics
5.1 |  | General rated characteristics |  | The enclosure complies with all requirements in §5.1 | references in chapter 2 of C2/115-3 NBN EN 206 NBN B 15-001 NBN EN 13369 NBN series EN(V) 1990 to 1992 (structural Eurocodes)
|  |  | Will condensation be prevented by design, or reduced? |  |  | (indicate compliant or non-applicable in column I) |  | If condensation is unavoidable: discribe the measures taken
|  |  | Resistance to short-term stresses |  |  |  |  | If based on an increased factor of 1.3 in strength, please describe for which material/partson
5.2 |  | Degree of protection of enclosures |  | The enclosure complies with all requirements in §5.2; (minimum degree of protection is IP23D) | NBN EN 62271-202 section 6.14 NBN EN 60529 |  |  | If IP class differs from IP23D, please specify
5.3 |  | Protection of the prefabricated substation against mechanical stress |  | The enclosure complies with all requirements in §5.3 | Eurocode 1 NBN EN 62271-202 section 6.101 NBN EN 62271-1 NBN EN 62262 |  |  | If any deviation, please specify
6 |  | Design and construction
6.2 |  | Fire behaviour |  | The enclosure complies with all requirements in §6.2 | KB / AR 07.07.1994 NBN EN 62271-202 section 6.104.2 and 6.104.2.3 AREI/RGIE Eurocode 1 Eurocode 2 |  |  | If any deviations: please specify
|  |  | Non-flammable materials |  | NBN EN 62271-202 section 6.104.2 AREI/RGIE |  |  | Describe all materials used in the enclosure in annex Folder A & fill in tab 4 Proof of conformity
|  |  | Are synthetic materials, or materials other than the non-flammable as described in §6.2 used? subject to agreement by Synergrid |  | NBN EN 62271-202 section 6.104.2.3 | Technical data sheet(s) |  | Describe all synthetic materials used in the enclosure in annex Folder B & fill in tab 4 Proof of conformity
6.3 |  | Thermal isolation and condensation |  | The enclosure complies with all requirements in §6.3 | NBN EN 62271-1 for normal operating conditions
|  |  | Additional measures necessary? (thermal insulation, adequate ventilation, targeted heating and thermal regulation, …) |  |  |  |  | If additional measures, describe the additionnal measures taken
6.4 |  | Building materials |  | The enclosure complies with all requirements in §6.4 | references in chapter 2 of C2/115-3
|  |  | Are alternative normative references used to prove compliance? Subject to approval by Synergrid |  |  | Test report(s) |  | if alternative normative reference are used, Specify the used references and prove the equivalence
6.5 |  | Concrete composition and treatment |  | The enclosure complies with all requirements in §6.5 and its subchapters
| 6.5.2 | Reinforcement | Subject to approval by Synergrid |  | NBN EN 1992-1-1 | Technical data sheet |  | Description of the type of reinforcement + technical data sheets, certificates of conformity an certificate of origin. Add the information in annex Folder C & fill in tab 4 Proof of conformity
| 6.5.3 | Concrete composition | Consistency class and grain size |  | NBN EN 206 Annex A of NBN EN 13369 (environmental condition E, high aggressiveness) | Technical data sheet |  | Specify information about consistency classes and grain size, and their impact on the durability requirements. Add this in annex Folder D & fill in tab 4 Proof of conformity
6.8 |  | Functional openings |  | The enclosure complies with all requirements in §6.8 and its subchapters
| 6.8.1 | Doors | Degree of protection when closed |  | NBN EN 62271-202 section 6.104.4 | Technical data sheet |  | Specify technical information on the door/frame; add this in annex Folder E & fill in tab 4 Proof of conformity
|  |  | Non-walk-in enclosures: Indicate the dimensions of the door opening in column J |  |  |  |  | Indicate the dimensions of the door opening
|  |  | Opening angles when locked in open position; indicate the angles | At least 90° and also at an angle of at least 160° |  |  |  | Specify the angles
|  |  | Are all doors replaceble by panels? |  |  |  |  | Specify the optional panels
| 6.8.2 | Ventilation openings |  |  | NBN EN 62271-202 section 6.104.5 | Technical data sheet |  | Specify technical information on and location of the ventilation openings; add this in annex Folder F & fill in tab 4 Proof of conformity
|  |  | Degree of protection | minimum IP23D |  |  |  | Indicate the degree of protection
|  |  | Number and dimensions ventilation openings | minimum 2 ventilation openings |  | Plans / drawings |  | Specify the ventilation openings + reference plans/drawings
| 6.8.3 | Cable entries | Location, size, number and position of the cable entries for the cables |  |  | Plans / drawings |  | Specify information on the location, size and number of the cable entries; add this in annex Folder G & fill in tab 4 Proof of conformity
|  |  | Waterproof entry of both ends of the earth loop | The earth loop connection complies with all requirements in §6.8.3 |  |  |  | Specify information on the type and location of the earth loop connection; add this in annex Folder H & fill in tab 4 Proof of conformity
6.9 |  | Volume of the enclosure |  | The enclosure complies with all requirements in §6.9 |  | Plans / drawings |  | Specify the reference off the plans/drawings
|  |  | external width x depth | maximum 2.25m x 1.25m |  | Plans / drawings |  | Specify the reference off the plans/drawings
|  |  | external height | maximum 2m |  | Plans / drawings |  | Specify the reference off the plans/drawings
6.10 |  | Cellar |  | The enclosure complies with all requirements in §6.10 |  |  |  | Specify informationon (and proof) of the water tighteness; add this in annex Folder J & fill in tab 4 Proof of conformity
|  |  | water tightness | minimum 10 years waterproof guaranteed |  |  |  | Indicate the guaranteed minimum period
|  |  | does the enclosure consist of 2 serapable parts? |  |  | (indicate compliant or non-applicable in column I)
|  |  | if the enclosure consist of 2 separable parts: | guaranteed sealing, and no water ingress in cellar |  |  |  | Describe the method/system used to achieve this; add this information in annex folder J & fill in tab 4 Proof of conformityh
6.11 |  | Floor slab |  | The enclosure complies with all requirements in §6.11
| 6.11.1 |  | functional openings |  |  | Plans / drawings |  | Specify information about type position and dimensions of functional openings + reference plans/drawings; add this in annex Folder K & fill in tab 4 Proof of conformity
6.12 |  | Roof |  | The enclosure complies with all requirements in §6.12
|  |  | water tightness | minimum 10 years waterproof guaranteed. |  | Test report / declaration |  | Add information in annex folder L & fill in tab 4 Proof of conformity
|  |  | construction design; roof in one piece? |  |  | (indicate compliant or non-applicable in column I)
|  |  | fixed to the walls,? |  |  |  |  | Add information in annex folder L & fill in tab 4 Proof of conformity
|  |  | instructions for disassembly, removal and re-assembly |  |  | Instructions for disassembly, removal and re-assembly |  | Add the information in annex Folder L & fill in tab 4 Proof of conformity
|  |  | lifting system of the roof |  |  | technical discription of roof anchor points |  | Add the information in annex Folder L & fill in tab 4 Proof of conformity
|  |  | inclination of flat roof | minimum 2% (2cm/m) inclination, towards water drainage. Indication of roof inclination present on drawings. |  | Plans / drawings |  | Add the information in annex Folder L & fill in tab 4 Proof of conformity
6.13 |  | Resistance to ageing and corrosion |  | The enclosure complies with all requirements in §6.13 and its subchapters | NBN EN 62271-202 section 6.104.3 | Procedure |  | Add the anti-aging procedures for the switching room in annex Folder M & fill in tab 4 Proof of conformity
| 6.13.2 | maintenance | Functional openings | process compliant to the requirements in §6.13.2 | NBN EN 62271-202 section 6.104.3 NBN EN ISO 12944-2, code C4 High RoHS directive Qualanod & Qualicoat specs | Discription of the proces |  | Discription of the proces (incl preliminary treatments) + used products in folder M & fill in tab 4 Proof of conformity
|  |  | If maintenance is necessary for rotating / movable parts, describe the maximum needed time interval between two maintenance sessions | at least 10 years. |  |  |  | Specify the needed interval for maintenaince
|  |  | Are alternative corrosion protections proposed? Subject to approval by Synergrid | process compliant to the requirements in §6.13.2 |  |  |  | If yes, specify describtion and demonstrate equivalence; add this in annex Folder M & fill in tab 4 Proof of conformity
| 6.13.3 |  | Door & door frame | Painted version must be proposed |  | Test Report(s) |  | Specify the reference of the applicable test reports
| 6.13.4 |  | Frame, rails, screws and other fastening elements Are alternative corrosion protections are subject to approval by Synergrid |  | NBN EN ISO 12944-2, code C4 High NBN EN ISO 1461 |  |  | Specify information on used corrosion protection for these parts; add information in annex Folder M & fill in tab 4 Proof of conformity (Are alternative corrosion protections proposed? Describe and demonstrate equivalence)
6.14 |  | Earthing and equipotential connections |  | The enclosure complies with all requirements in §6.14 and its subchapters | AREI/RGIE book 2 sections 2.3.2 & 5.4 or book 3 sections 4.2.5.2 & 5.5 NBN EN 62271-202 section 6.3
|  |  | suitable earthing system? |  |  |  |  | Indicate here if the enclosure is suitable for a global earthing system, a non-global earthing system or for both
continuity of the earthing system guaranteed during the lifetime of the enclosure
|  |  | general earthing disconnector |  |  | Plans / drawings |  | Specify the reference of the plans / drawings where the position of the general earting indicator is visible
|  |  | for non-global earthing: insulation levels of the external walls for enclosures | compliant to the requirements in §6.14.2 |  |  |  | Describe the measures and isolation levels, add information in annex Folder N & fill in tab 4 Proof of conformityi
6.15 |  | Nameplates |  | The enclosure complies with all requirements in §6.15 | NBN EN 62271-202, section 6.11
|  |  | Design example of the nameplate: Subject to approval by Synergrid |  |  | Plans / drawings |  | Specify an example of the used nameplate in annex Folder O & fill in tab 4 Proof of conformity
6.16 |  | Drawing and arrangement of enclosure |  | The drawings comply with all requirements in §6.16 |  | Plans / drawings |  | Add all the drawings in annex Folder P & fill in tab 4 Proof of conformity
7 |  | Type test reports
7.1 |  | General provisions | Requirements for a valid test report | All the Specifyn test reports are from an accredited laboratory following ISO 17025 |  | (indicate compliant or non-applicable in column I)
7.2 |  | Corrosion resistance for the enclosure’s metallic elements (and their frames) | Qualicoat certification | Proof of the certication |  | Qualicoat certification |  | Specify here the reference of the certification; add certification in annex Folder Q & fill in tab 4 Proof of conformity
|  |  | Qualinod certification | Proof of the certification |  | Qualinod certification |  | Specify here the reference of the certification; add certification in annex Folder Q & fill in tab 4 Proof of conformity
|  |  | Galvanisation of steel parts | Proof of the galvanisation | NBN EN ISO 1461 | Attestation of a statement |  | Specify here the reference of the attestation/statement; add document in annex Folder Q & fill in tab 4 Proof of conformity
|  |  | conformity with the RoHS directive | Proof of the conformity | RoHS directive | Attestation of a statement |  | Specify here the reference of the attestation/statement; add document in annex Folder Q & fill in tab 4 Proof of conformity
7.3 |  | Verification of degree of protection (IP-x-code) | ventilation openings | IP 23D | NBN EN 62271-202 section 7.7 | Test Report / certificate |  | Specify here the reference of the test report; add report in annex Folder R & fill in tab 4 Proof of conformity
7.4 |  | Mechanical impact test (IK-code) | all external places of the enclosure (doors, covers, ventilation, hinges,…) | IK10 | NBN EN 62271-202 section 7.101.3 | Test Report / certificate |  | Specify here the reference of the test report; add report in annex Folder S & fill in tab 4 Proof of conformity
7.5 |  | Verification of insulation resistance of the building's exterior walls and functional openings for enclosures for non-global earthing | insulation compliant with the requirements of subchapter 6.14.2 | test procedure and test report compliant with subchapter 9.2 Annex B: Insulation tests of the building's exterior walls | IEC 60364-6 NBN EN 62271-304 for classes 3 and 4 | Test Report |  | Specify here the reference of the test report; add report in annex Folder T & fill in tab 4 Proof of conformity
8 |  | Computed simulation - calculation notes
8.2 |  | Calculation notes – mechanical and pressure resistance of the enclosure | pressure withstand of the entire construction (walls, cellar, roof, or a floor slab if present, etc.) | compliant with §5.3 (Protection of the prefabricated substation against mechanical stress) and §5.5 (Internal arc withstand) | Eurocode 1 NBN EN 62271-202 section 6.101 | Calculation note |  | Add the calculation notes in annex Folder V & fill in tab 4 Proof of conformity
|  |  | Wind pressure withstand strength | at least 34m/s | Eurocode |  |  | Specify the windspeed used in the calculations
|  |  | Roof loads withstand strength | minimum 250daN/m² | Eurocode |  |  | Specify the roofload used in the calculations
|  |  | Snow loads withstand strength; the snow loads and ice loads have to be taken into account | Calculations note according to the Eurocode - specify the reference of the applicable document(s) in column J sk = 1 kN/m² | Eurocode | (indicate compliant or non-applicable in column I)
|  |  | Floor loads withstand strength; the loads of the switchgear has to be taken into account |  | Eurocode | (indicate compliant or non-applicable in column I)
9 |  | Annexes
9.2 |  | Annex B: Insulation tests of the building's exterior walls | Test requirements §7.5 for a non global earthing system |  |  |  |  | Specify information; add this in annex Folder W & fill in tab 4 Proof of conformity
compliant
non-compliant
EXPLANATIONS FOR COMPLETING THIS CHECKLIST | [6 empty] | non applicable
Column |  | Title | Remarks
B - C |  | Reference in C2/115-3 ed1.0 (01.04.2021) | Reference to the relevant section in the text of C2/115-3 ed1.0 (01.04.2021).
D - E - F - G |  | Characteristic Requirement Normative reference | See relevant section in the text of C2/115-3 ed1.0 (01.04.2021) for a full description.
The following options are possible:
1. A declaration of honour by the manufacturer regarding conformity with the requirement is sufficient. In this case, the filling in of column I in combination with the signing of the conformity declaration in the first tab applies as the declaration of honour of the manufacturer. There is no need for a separate document for this (the grey background is a visual reminder that there is no separate proof document required).
2. A certificate or test report is required. For the type test reports as required in chapter 7, the general provisions in §7.1 of C2/115-3 ed1.0 (01.04.2021) concerning a valid type test report apply.
For certain requirements, C2/115-3 ed1.0 (01.04.2021) allows to propose certificates or test reports based on other normative references, on the conditions that - the equivalence is proved by the manufacturer; - they are compliant with the conditions for a valid proof of conformity as mentioned below.
H |  | Required proof of conformity | 3. Plans / drawings. See §6.17 of C2/115-3 ed1.0 (01.04.2021)
4. Calculation note. See §8 of C2/115-3 ed1.0 (01.04.2021)
5. Other document or information: see details in corresponding paragraph of C2/115-3 ed1.0 (01.04.2021)
Conditions for a valid proof of conformity: - to be available in Dutch, French, English or German. Other languages are not accepted. - to be available as a separate document in the technical file. Hyperlinks to online documents without the presence of the document itself, or to web pages, are not accepted as valid proof of conformity. - a document with a unique file name (reference), included in the list of proofs of conformity in tab 4, together with an explanation of the content of the document. - additional: conditions for a valid type test report: see tab 1 (declaration of conformity)
I |  | C2/115-3 Compliant? | The filling in of column I in combination with the signing of the declaration of conformity in the first tab applies as the declaration of honour of the manufacturer concerning the conformity of the units with the relevant paragraph in C2/115-3 ed1.0 (01.04.2021).
J |  | Manufacturer’s reference of proof of conformity | Each piece of evidence used to demonstrate the required conformity shall have a unique reference number, specified in this column. However, the same piece of evidence may be used as evidence for more than one requirement if its contents permit it. Each supporting document mentioned in this column must be completed in the 4th tab "proofs of conformity" together with an explanation, and must be present as a separate document in the technical file. See tab 4 "Proofs of conformity" .
J |  | Additional information | Here the manufacturer has room for explanations: - mandatory information if indicated in column F - a free explanatory note if the manufacturer judges it necessary. - a reference to an annex to be created in which the requested information should be placed
K, L |  | Evaluation Synergrid | This column can be filled in by Synergrid during the study of the homologation application.
COLOR LEGEND
Mandatory field to be filled in
| text | Mandatory field to be filled in
Voluntary field to be filled in
Reserved for Synergrid
| text | Title
| text | Title
| text | Informative text field
| text | Information for the applicant
Empty field; no action required
Note on G76: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Remplacer par NBN EN 60259

## 4. proofs of conformity
PREFABRICATED ENCLOSURES TO BE HOMOLOGATED FOR LIST C2/115-0 ACCORDING TO THE REQUIREMENTS OF THE TECHNICAL SPECIFICATION C2/115-3.2 ed1 (05/2025)
4. Composition of the technical file: list of document references of the proofs of conformity referred to in the checklist (tab 3; columns H and J).
The filename of each document must start with the Doc Ref (from column D) followed with the manufacturer reference (column E). For exemple: B2-"manufacturer reference".doc
For an explanation of the used colour code: see tab 1 GLV
GLV |  |  | (brand name) | (series name - one or more series)
The line Ax, Bx, Cx, etc can be freely copied to increase the number of documents in the corresponding attachment
Name of the annexe | The pragraphs it refers to | Doc. Ref. | Manufacturer-references of the proofs of conformity according to the references given in column J of the checklist C2/115-3 | Description | (Foreseen) date of introduction to Synergrid (see also C2/115-1, §2.2)
Folder A | 6.2 | A1
A2
A x
Folder B | 6.2 | B1
B2
B x
Folder C | 6.5.2 | C1
C2
C x
Folder D | 6.5.3 | D1
D2
D x
Folder E | 6.8.1 | E1
E2
E x
Folder F | 6.8.2 | F1
F3
F x
Folder G | 6.8.3 | G1
G2
G x
Folder H | 6.8.3 | H1
H2
H x
Folder I | 6.8.4 | I1
I2
I x
Folder J | 6.10 | J1
J2
J x
Folder K | 6.11.1 | K1
K2
K x
Folder L | 6.12 | L1
L2
L x
Folder M | 6.13 | M1
M2
M x
Folder N | 6.14 | N1
N2
Nx
Folder O | 6.15 | O1
O2
Ox
Folder P | 6.16 | P1
P2
Px
Folder Q | 7.2 | Q1
Q2
Q3
Q4
Qx
Folder R | 7.3 | R1
R2
Rx
Folder S | 7.4 | S1
S2
Sx
Folder T | 7.5 | T1
T2
Tx
Folder V | 8.2 | V1
V2
V x
Folder W | 9.2 | W1
W2
W x
Folder X | FREE | X1
X2
Xx