## cover page
C2/113
Classification and homologation procedure for MV switchgear
according to the technical specification C2/112
Part 3
Ratings and tests for HV switchgear,
intended for use in a Client installation to be connected to
the public HV distribution grid of a Belgian DSO
-
Assessment Guide
Edition 2 - DPC (10.2023)

## assessment guide
Assessment Guide for homologation of HV switchgear according the Technical File C2/113-3 ED.2-DPC
The Assessment Guide shall be completed based on the instructions given in §3 of document C2/113-3 - Technical File | [8 empty] | Also refers to the protection of the unique | Also refers to the protection of the unique
[9 empty] | transformer in a Client installation | transformer in a Client installation
Switchgear family name | [6 empty] | Busbar upstream the Gen. Protection | Loop Connection | General Protection | General Protection | Feeder DSO | Billing metering function | FU downstream the General Protecton
GIS or AIS | [5 empty] | Functional Unit (FU) |  | FU K | FU T | FU DxT | FU DxN | FU M | such as FU R, K, T, DxT, P (except FU M)
1st AA category | [5 empty] | Synergrid scheme FU
2nd AA category |  |  |  | (if applicable) |  | Manufacturer's designation
AA category FU M |  |  |  | (if applicable and different from 1st and 2nd AA category) |  | Rated current Irbb (A)
Single rating or dual ratings | [5 empty] | Rated current FU Ir (A)
Folder | Item No. | NBN EN 62271-xxx (Sub)clause(s) | Test or verification | Specific test specifications: Refer to techncial file C2/113-3 ED.2 | Rated value(s) for which the homologation is requested: To be completed by the Applicant | ISO 17025 Refer to Technical file C2/113-3 § 2.2 | Busbar upstream the General Protection | Loop Connection FU K | General Protection FU T | General Protection FU DxT | Feeder DSO FU DxN | Billing metering function FU M | FU downstream the General Protection such as FU R, K, T, DxT, P (except FU M)
B | - | 62271 -200 7.2 | Dielectric tests | - | Ur = … kV
| 1 | 62271 -200 7.2.6 7.2.7 | Power-frequency voltage withstand tests (Ud) Lightnig impulse voltage withstand tests (Up) Ud & Up : - phase-to-earth & between phases - accross the isolating distance Refer to Technical file C2/113-3 § 4.2 | - |  | YES
| 2 | 62271 -200 7.2.10 & Annex B | Partial discharges measurement test | Refer to technical file C2/113-3 § 5.2.1 |  | NO
| 3 | 62271 -200 7.2.101 | Dielectric test on cable testing circuits (Uct,DC) Refer to Technical file C2/113-3 § 4.2 | Refer to technical file C2/113-3 § 5.2.2 |  | NO
C | 1 | 62271 -200, -100, -102, -103, -105 7.4 7.5 | Continuous current tests Refer to Technical file C2/113-3 § 4.2 | - | Irbb = … A FU K : Ir = … A FU T: Ir = … A FU DxG : Ir = … A FU DxN : Ir = … A | YES
D | 1 | 62271 -200, -100, -102, -103, -105 7.6 | Short-time withstand current and peak withstand current tests on main circuits Refer to Technical file C2/113-3 § 4.2 | Refer to technical file C2/113-3 § 5.3 | Single rating : - GIS : - 20 kA @ 24 kV or - 25 kA @ 12 kV - AIS : - 20 kA @ 24 kV or - 20 kA @17,5 kV or - 25 kA @ 12 kV Dual ratings : - GIS : - 20 kA @ 24 kV + 25 kA @ 12 kV or - 25 kA @ 24 kV - AIS : - 20 kA @ 24 kV + 25 kA @ 12 kV or - 25 kA @ 24 kV or - 20 kA @ 17.5 kV + 25 kA @ 12 kV or - 25 kA @ 17.5 kV [Remark : the choice will be presented in a drop-down list] | YES
E | 1 | 62271 -200 7.7.1 | Verification of the IP degree of protection | Refer to technical file C2/113-3 § 5.4 Only a declaration of conformity is required |  | NO
| 2 | 62271 -200 7.7.2 | Verification of the IK degree of protection | Refer to technical file C2/113-3 § 5.4 Only a declaration of conformity is required |  | NO
F | 1 | 62271 -200 7.8 60068-2-17 8.5.2 | Tightness test at 40°C on every sealed pressure gas-filled compartment | Refer to technical file C2/113-3 § 5.5 | Pre = … bar rel Pme = … bar rel | NO
K | 1 | 62271 -100 7.102 to 7.107 7.2.12.102 7.4.4.2 | Verification of short-circuit making and breaking capacities of circuit-breaker Test duties T10, T30, T60, T100s, T100a Refer to Technical file C2/113-3 § 4.2 | - | Shall comply with item D.1 | YES
| 2 | 62271-100 7.111.9 | Verification of capacitive cable charging current making and breaking capacities of circuit-breaker Test duties CC1 & CC2 Refer to Technical file C2/113-3 § 4.2 | - | Icc = … A | YES
| 3 | 62271-100 7.112.1 | Electrical endurance test on class E2 circuit breakers not for auto-reclosing (O - 3 min - CO - 3 min - CO) Refer to Technical file C2/113-3 § 4.2 | - | Ima / Isc Single rating : - GIS : - 50 kÂ / 20 kA @ 24 kV or - 62.5 kÂ / 25 kA @ 12 kV - AIS : - 50 kÂ / 20 kA @ 24 kV or - 50 kÂ / 20 kA @ 17.5 kV or - 62.5 kÂ / 25 kA @ 12 kV Dual ratings : - GIS : - 50 kÂ / 20 kA @ 24 kV + 62.5 kÂ / 25 kA @ 12 kV or - 62.5 kÂ / 25 kA @ 24 kV - AIS : - 50 kÂ / 20 kA @ 24 kV + 62.5 kÂ / 25 kA @ 12 kV or - 62.5 kÂ / 25 kA @ 24 kV - 50 kÂ / 20 kA @ 17.5 kV + 62.5 kÂ / 25 kA @ 12 kV or - 62.5 kÂ / 25 kA @ 17.5 kV [Remark : the choice will be presented in a drop-down list] | YES
| 4 | 62271-100 7.112.2 | Electrical endurance test on class E2 circuit breakers for rapid auto-reclosing duty (O - 0.3s - CO - 15s - CO) Refer to Technical file C2/113-3 § 4.2 | - | Ima / Isc Single rating : - GIS : - 50 kÂ / 20 kA @ 24 kV or - 62.5 kÂ / 25 kA @ 12 kV - AIS : - 50 kÂ / 20 kA @ 24 kV or - 50 kÂ / 20 kA @ 17.5 kV or - 62.5 kÂ / 25 kA @ 12 kV Dual ratings : - GIS : - 50 kÂ / 20 kA @ 24 kV + 62.5 kÂ / 25 kA @ 12 kV or - 62.5 kÂ / 25 kA @ 24 kV - AIS : - 50 kÂ / 20 kA @ 24 kV + 62.5 kÂ / 25 kA @ 12 kV or - 62.5 kÂ / 25 kA @ 24 kV - 50 kÂ / 20 kA @ 17.5 kV + 62.5 kÂ / 25 kA @ 12 kV or - 62.5 kÂ / 25 kA @ 17.5 kV [Remark : the choice will be presented in a drop-down list] | YES
| 5 | 62271-103 7.101.1 | Making and breaking tests class E3 of general purpose switch. Refer to Technical file C2/113-3 § 4.2 | - | Iload = … A Icc = … A Ima Single rating : - GIS : - 50 kÂ @ 24 kV or - 62.5 kÂ @ 12 kV - AIS : - 50 kÂ @ 24 kV or - 50 kÂ @ 17.5 kV or - 62.5 kÂ @ 12 kV Dual ratings : - GIS : - 50 kÂ @ 24 kV + 62.5 kÂ @ 12 kV or - 62.5 kÂ @ 24 kV - AIS : - 50 kÂ @ 24 kV + 62.5 kÂ @ 12 kV or - 62.5 kÂ @ 24 kV - 50 kÂ @ 17.5 kV + 62.5 kÂ @ 12 kV or - 62.5 kÂ @ 17.5 kV [Remark : the choice will be presented in a drop-down list] | YES
| 6 | 62271-102 7.101 | Short-circuit making current test class E2 of earthing-switch. Refer to Technical file C2/113-3 § 4.2 | - | Ima Single rating : - GIS : - 50 kÂ @ 24 kV or - 62.5 kÂ @ 12 kV - AIS : - 50 kÂ @ 24 kV or - 50 kÂ @ 17.5 kV or - 62.5 kÂ @ 12 kV Dual ratings : - GIS : - 50 kÂ @ 24 kV + 62.5 kÂ @ 12 kV or - 62.5 kÂ @ 24 kV - AIS : - 50 kÂ @ 24 kV + 62.5 kÂ @ 12 kV or - 62.5 kÂ @ 24 kV - 50 kÂ @ 17.5 kV + 62.5 kÂ @ 12 kV or - 62.5 kÂ @ 17.5 kV [Remark : the choice will be presented in a drop-down list] | YES
L | 1 | 62271-102 7.102 | Mechanical endurance test for disconnector Refer to Technical file C2/113-3 § 4.2 | - | Class M … | NO
| 2 | 62271-102 7.102 | Mechanical endurance test for earthing switch Refer to Technical file C2/113-3 § 4.2 | - | Class M … | NO
| 3 | 62271-103 7.102.1 7.102.2.1 7.103 | Mechanical endurance test for switch-disconnector Refer to Technical file C2/113-3 § 4.2 | - | Class M … | NO
| 4 | 62271-100 7.101.2 7.101.2.3 7.2.12.102 | Mechanical endurance test for circuit-breaker Refer to Technical file C2/113-3 § 4.2 | - | Class M … | NO
| 5 | 62271-200 & Amd 1 7.102.2 62271-1 6.6.4 62271-102 6.105 | Maximum allowable force for operation | Refer to technical file C2/113-3 § 5.6 |  | NO
M | 1 | 62271-200 & Amd 1 7.102.2 | Mechanical and electromechanical interlocks | Refer to technical file C2/113-3 § 5.7 |  | NO
| 2 | 62271-200 & Amd 1 7.102.2 | Mechanical and electromechanical interlocks with motorized operating mechanism | Refer to technical file C2/113-3 § 5.7 |  | NO
N | 1 | 62271-102 7.105 | Kinematic chain of disconnector & switch-disconnector | - |  | NO
| 2 | 62271-102 7.105 | Kinematic chain of earthing-switch | - |  | NO
O | 1 | 62271-200 & Amd 1 7.103.1 | Pressure withstand test for gas-filled compartments | Refer to technical file C2/113-3 § 6.2 for FU M AA10 | Shall comply with folder F | NO
P | 1 | 62271-200 7.104.3 | Measurements of leakage currents on accessible side of insulating partitions Only applicable for AIS switchgear | Refer to technical file C2/113-3 § 5.8 |  | NO
Q | - | 62271-200 7.105 & annex A | Internal arc tests Internal arc tests are mandatory, except for FU M intended to be used exclusively downstream a general protection with switch-fuse combination | Refer to technical file C2/113-3 § 5.9.1 Refer to technical file C2/113-3 § 6.3.2 for FU M
Q10. | - |  | Internal arc test for switchgear of category AA10 | Refer to technical file C2/113-3 § 5.9.2
| 1 |  | Internal arc test with arc ignition in the gas filled compartment Refer to Technical file C2/113-3 § 4.2 | Refer to technical file C2/113-3 § 5.9.2.1 Refer to technical file C2/113-3 § 6.3.1 for FU M AA10 | IAC A FL ... kA, 1s (IA, tA) IAC A FLR … kA, 1s (IA, tA) | YES
| 2 |  | Internal arc test with arc ignition in the cable compartment Refer to Technical file C2/113-3 § 4.2 | Refer to technical file C2/113-3 § 5.9.2.2 Cable compartment of FU T: no IAC | IAC A FL … kA, 1s (IAe, tAe) IAC A FLR … kA, 1s (IAe, tAe) | YES
| 3 |  | Internal arc test with arc ignition in the specific screened solid insulated busbar compartment or lateral extension component out of the gas-filled compartment (if applicable) Refer to Technical file C2/113-3 § 4.2 | Refer to technical file C2/113-3 § 5.9.2.3 | IAC A FL … kA, 1s (IAe, tAe) IAC A FLR … kA, 1s (IAe, tAe) | YES
| 4 |  | Demonstration of the pressure withstand of all elements involved in or that can communicate with the gas exhaust path (e.g. ducts, compartments and AA10-R riser base frame), with arc ignition in the sealed pressure gas-filled compartment. | Refer to technical file C2/113-3 § 5.9.2.4 | Shall comply with item Q10.1 | YES
| 5 |  | Internal arc test with arc ignition in the metering compartment Refer to Technical file C2/113-3 § 4.2 | Refer to technical file C2/113-3 § 5.9.2.5 Refer to technical file C2/113-3 § 6.3.2 for FU M AA10 | IAC A FL … kA, 1s (IAe, tAe) IAC A FLR … kA, 1s (IAe, tAe) | YES
Q11. | - |  | Internal arc test for switchgear of category AA11 | Refer to technical file C2/113-3 § 5.9.3
| 1 |  | Internal arc test with arc ignition in the gas filled compartment Refer to Technical file C2/113-3 § 4.2 | Refer to technical file C2/113-3 § 5.9.3.1 | IAC A FL ... kA, 1s (IA, tA) IAC A FLR … kA, 1s (IA, tA) | YES
| 2 |  | Internal arc test with arc ignition in the cable compartment Refer to Technical file C2/113-3 § 4.2 | Refer to technical file C2/113-3 § 5.9.3.2 Cable compartment of FU T: no IAC | IAC A FL … kA, 1s (IAe, tAe) IAC A FLR … kA, 1s (IAe, tAe) | YES
| 3 |  | Internal arc test with arc ignition in the specific screened solid insulated busbar compartment or lateral extension component out of the gas-filled compartment (if applicable) Refer to Technical file C2/113-3 § 4.2 | Refer to technical file C2/113-3 § 5.9.3.3 | IAC A FL … kA, 1s (IAe, tAe) IAC A FLR … kA, 1s (IAe, tAe) | YES
| 4 |  | Demonstration of the pressure withstand of all elements involved in or that can communicate with the gas exhaust path (e.g. ducts, compartments and AA11-R riser base frame), with an arc in the sealed pressure gas-filled compartment. | Refer to technical file C2/113-3 § 5.9.3.4 | Shall comply with item Q11.1 | YES
Q13. | - |  | Internal arc test for switchgear of category AA13 | Refer to technical file C2/113-3 § 5.9.4
| 1 |  | Internal arc test with arc ignition in the gas filled compartment Refer to Technical file C2/113-3 § 4.2 | Refer to technical file C2/113-3 § 5.9.4.1 | IAC A FL ... kA, 1s (IA, tA) IAC A FLR … kA, 1s (IA, tA) | YES
| 2 |  | Internal arc test with arc ignition in the cable compartment Refer to Technical file C2/113-3 § 4.2 | Refer to technical file C2/113-3 § 5.9.4.2 Cable compartment of FU T: no IAC | IAC A FL … kA, 1s (IAe, tAe) IAC A FLR … kA, 1s (IAe, tAe) | YES
| 3 |  | Internal arc test with arc ignition in the specific screened solid insulated busbar compartment or lateral extension component out of the gas-filled compartment (if applicable) Refer to Technical file C2/113-3 § 4.2 | Refer to technical file C2/113-3 § 5.9.4.3 | IAC A FL … kA, 1s (IAe, tAe) IAC A FLR … kA, 1s (IAe, tAe) | YES
| 4 |  | Demonstration of the pressure withstand of all elements involved in or that can communicate with the gas exhaust path (e.g. evacuation duct, compartments), with an arc in the sealed pressure gas-filled compartment. | Refer to technical file C2/113-3 § 5.9.4.4 | Shall comply with item Q13.1 | YES
Q15. | - |  | Internal arc test for switchgear of category AA15 | Refer to technical file C2/113-3 § 5.9.5
| 1 |  | Internal arc test with arc ignition in the gas filled compartment Refer to Technical file C2/113-3 § 4.2 | Refer to technical file C2/113-3 § 5.9.5.1 | IAC A FL ... kA, 1s (IA, tA) IAC A FLR … kA, 1s (IA, tA) | YES
| 2 |  | Internal arc test with arc ignition in the cable compartment Refer to Technical file C2/113-3 § 4.2 | Refer to technical file C2/113-3 § 5.9.5.2 Cable compartment of FU T: no IAC | IAC A FL … kA, 1s (IAe, tAe) IAC A FLR … kA, 1s (IAe, tAe) | YES
| 3 |  | Internal arc test with arc ignition in the specific screened solid insulated busbar compartment or lateral extension component out of the gas-filled compartment (if applicable) Refer to Technical file C2/113-3 § 4.2 | Refer to technical file C2/113-3 § 5.9.5.3 | IAC A FL … kA, 1s (IAe, tAe) IAC A FLR … kA, 1s (IAe, tAe) | YES
| 4 |  | Demonstration of the pressure withstand of all elements involved in or that can communicate with the gas exhaust path (e.g. ducts, compartments, AA15-A absorber base frame), with an arc in the sealed pressure gas-filled compartment. | Refer to technical file C2/113-3 § 5.9.5.4 | Shall comply with item Q15.1 | YES
Q20. | - |  | Internal arc test for switchgear of category AA20 | Refer to technical file C2/113-3 § 5.9.6
| 1a |  | Three-phase internal arc test with arc ignition in the gas-filled compartment for an arc test current equal to 4.8 kA Refer to Technical file C2/113-3 § 4.2 | Refer to technical file C2/113-3 § 5.9.6.1 | IAC A FL ... kA, … ms (IA, tA) IAC A FLR … kA, …ms (IA, tA) | YES
| 1b |  | Three-phase internal arc test with arc ignition in the gas-filled compartment for an arc test current equal to 100% of the arc fault current IA Refer to Technical file C2/113-3 § 4.2 | Refer to technical file C2/113-3 § 5.9.6.2 | IAC A FL ... kA, … ms (IA, tA) IAC A FLR … kA, …ms (IA, tA) | YES
| 2 |  | Internal arc test with arc ignition in the cable compartment (1) either without an arc mitigation system or with an arc mitigation system not in service (2) or with an arc mitigation system in service Refer to Technical file C2/113-3 § 4.2 | Refer to technical file C2/113-3 § 5.9.6.3 | Either (1): - IAC A FL … kA, 1s (IAe, tAe) - IAC A FLR … kA, 1s (IAe, tAe) Or (2): - IAC A FL … kA, … ms (IAe, tAe) - IAC A FLR … kA, … ms (IAe, tAe) | YES
| 3 |  | Internal arc test with arc ignition in the specific screened solid insulated busbar compartment or lateral extension component out of the gas-filled compartment (if applicable) Refer to Technical file C2/113-3 § 4.2 | Refer to technical file C2/113-3 § 5.9.6.4 | IAC A FL … kA, 1s (IAe, tAe) IAC A FLR … kA, 1s (IAe, tAe) | YES
Q3x | - |  | Internal arc test for switchgear of category AA3x | Refer to technical file C2/113-3 § 5.9.7, -.8 and -.9
Q30. | 1 |  | Category AA30: Three-phase internal arc tests in all HV compartments (incl any component including the 3 phases in one single volume, if present) with arc test current equal to 100 % IA. Refer to Technical file C2/113-3 § 4.2 | Refer to technical file C2/113-3 § 5.9.7.1 Refer to technical file C2/113-3 § 6.3.2 for FU M AA3x | IAC A FL ... kA, 1s (IA, tA) IAC A FLR … kA, 1s (IA, tA) | YES
Q31. | 1 |  | Category AA31: Three-phase internal arc tests in all HV compartments (incl any component including the 3 phases in one single volume, if present) with arc test current equal to 100 % IA. Refer to Technical file C2/113-3 § 4.2 | Refer to technical file C2/113-3 § 5.9.8.1 Refer to technical file C2/113-3 § 6.3.2 for FU M AA3x | IAC A FL ... kA, 1s (IA, tA) IAC A FLR … kA, 1s (IA, tA) | YES
Q33. | 1 |  | Category AA33: Three-phase internal arc tests in all HV compartments (incl any component including the 3 phases in one single volume, if present) with arc test current equal to 100 % IA. Refer to Technical file C2/113-3 § 4.2 | Refer to technical file C2/113-3 § 5.9.9.1 Refer to technical file C2/113-3 § 6.3.2 for FU M AA3x | IAC A FL ... kA, 1s (IA, tA) IAC A FLR … kA, 1s (IA, tA) | YES
| 2 |  | Category AA33: Demonstration of the pressure withstand of all elements involved in or that can communicate with the gas exhaust path (e.g. evacuation ducts, compartments), with an arc in every compartment. | Refer to technical file C2/113-3 § 5.9.9.2 | Shall comply with item Q33.1 | YES
S | 1 | EN 62271-213 | Detection range of VDIS | Refer to technical file C2/113-3 § 5.10 |  | NO
W | 1 | - | Testing of HV CB overcurrent protection chain comprising a protection relay without auxiliary power supply or with dual power supply | Refer to technical file C2/113-3 § 5.11 |  | NO
X | 1 | EN 61869-2 7.2.201 | Current transformer - short-time thermal current (Ith) and dynamic current (Idyn) test Refer to Technical file C2/113-3 § 4.2 | Refer to technical file C2/113-3 § 6.4.1 | Ith = … kA - ... s Idyn = … kÂ | NO
| 2 | EN 61869-2 7.2.6 7.3.5.201 | Current transformer - Test for accuracy Refer to Technical file C2/113-3 § 4.2 | Refer to technical file C2/113-3 § 6.4.2 | CT ratio(s) = …/5A | NO
Y | 1 | EN 61869-3 7.2.6 7.3.5.301 | Voltage transformer - Test for accuracy Refer to Technical file C2/113-3 § 4.2 | Refer to technical file C2/113-3 § 6.5.1 | VT ratio(s) = …/Ѵ3 / 110/Ѵ3 V | NO