## 1 GLV
GLV |  | (brand name) | (model name)
DECLARATION OF CONFORMITY
C10/24 | Synchrocheck relays
based on the Synergrid prescription C10/11 ed2.4 (15/10/2025) and the corresponding technical specifications
The undersigned, |  | Manufacturer: |  | Represented by:
|  | Address: |  | Country:
email:
Telephone:
Hereby declares that the relay of this homologation application complies with the following conditions:
1. The relay complies with the relevant requirements set out in the Synergrid prescription C10/11 ed2.4 (15/10/2025).
2. The relay complies with the technical specifications C10/24 based on the Synergrid prescription C10/11 ed2.4 (15/10/2025). New developments and thus resulting requirements in the C10/11 prescription (master document and amendments) nothwithstanding they might not yet be reflected in the specifications, are applicable.
3. The technical file shall be drawn up on the basis of the Part 1 - Checklist, duly and correctly completed by the manufacturer, accompanied by all the required proof of conformity.
3.1 For technical requirements for which the required proof of conformity (column K in checklist) is a declaration of honour by the manufacturer, by signing and dating this declaration of conformity, the manufacturer confirms the correctness of the information (compliant / not compliant / not applicable) provided by him or her in columns L, M and N of this checklist.
2.2. For technical requirements for which the required proof of conformity (column K in checklist) is a report, a test report or a certificate, the necessary reports, test reports and/or certificates are available * in the technical file comply to the following requirements:
- Certificates have been issued by an EN 45011 (or ISO 17065:2012) certification body accredited for these materials.
- Test reports have been established by an ISO 17025:2005 or ISO 17065:2012 laboratory accredited for these tests.
2.3 A list of the document references or the certificates of conformity referred to in the checklist is also available in the technical file (see part 3).
Done at: |  | (location) |  | Homologated by Synergrid on:
On: |  | (date) |  | Stamp Synergrid & signature:
(stamp manufacturer & signature)

## 2 List of relays
C10/24 Synchrocheck relays based on the Synergrid prescription C10/11 ed2.4 (15/10/2025) and the corresponding technical specifications
REL | (brand name) | (model name)
1 | 2 | 3 | 4 | 5 | 6
SYNERGRID reference number (RELxxx-yy) | BRAND NAME | REFERENCE of the model / type of the unit | FIRMWARE VERSION | TYPE OF RELAY | Synergrid approval date
|  |  |  | C10/24 Synchrocheck relay | Date of homologation
X
EXPLANATIONS FOR THE COMPLETION OF THE TABLE
Column | Title | Remarks
1 | SYNERGRID reference number (RELxxx-yy-zzzz) | In the case of a positive homologation, each homologated relay is given a unique Synergrid reference number: xxx = unique reference or the manufacturer yy = serial number of manufacturer xxx's record xxx
2 | Brand name | Brand name under which the unit is marketed on the Belgian market.
3 | Reference of the model / type of the relay | Unique product name or reference. Units of the same product range must be unequivocally distinguished from each other through this name or reference.
4 | Firmware version | Reference of the firmware version of the relay.
5 | Type of relay | Put an "X" in the applicable categories
6 | Synergrid approval date Final homologation | Date on which the submitted homologation file was approved by Synergrid.

## 3 Notification of change
GLV |  | (brand name) | (model name)
NOTIFICATION OF CHANGE
C10/24 | Synchrocheck relays
based on the Synergrid prescription C10/11 ed2.4 (15/10/2025) and the corresponding technical specifications
The undersigned, |  | Manufacturer: |  | Represented by:
|  | Address: |  | Country:
email:
Telephone:
Hereby notifies that the already homologated relay complies with the following conditions:
1. The relay still complies with the relevant requirements set out in the Synergrid prescription C10/11 ed2.4 (15/10/2025).
2. The relay still complies with the technical specifications C10/24 based on the Synergrid prescription C10/11 ed2.4 (15/10/2025). New developments and thus resulting requirements in de C10/11 prescription (master document and amendments) nothwithstanding they might not yet be reflected in the specifications, are applicable.
3. The technical file shall be drawn up on the basis of the Part 1 - Checklist, completed for those requirements on which the change has or might have an impact, and accompanied by the required proof of conformity.
3.1 For technical requirements for which the required proof of conformity (column K in checklist) is a declaration of honour by the manufacturer, by signing and dating this declaration of conformity, the manufacturer confirms the correctness of the information (compliant / not compliant / not applicable) provided by him or her in columns L, M and N of this checklist.
3.2. For technical requirements for which the required proof of conformity (column K in checklist) is a report, a test report or a certificate, the necessary reports, test reports and/or certificates are available * in the technical file comply to the following requirements:
- Certificates have been issued by an EN 45011 (or ISO 17065:2012) certification body accredited for these materials.
- Test reports have been established by an ISO 17025:2005 or ISO 17065:2012 laboratory accredited for these tests.
3.3 A list of the document references or the certificates of conformity referred to in the checklist is also available in the technical file (see part 3).
Done at: |  | (location) |  | Homologated by Synergrid on:
On: |  | (date) |  | Stamp Synergrid & signature:
(stamp manufacturer & signature)

## Part 1 - Checklist
SPECIFICATION FOR SYNCHROCHECK RELAYS C10/24 (09/12/2025)
1. Checklist according to the requirements in Technical Prescriptions C10/11 ed2.4 (15/10/2025)
|  | (brand name) | (model name)
|  | Characteristic | Requirement | Reference C10/11 | C10/24 Synchronoscope relay | Required proof of conformity | C10/11 Compliant? | Manufacturer’s reference of proof of conformity | Required information | Evaluation Synergrid | Explanation Synergrid
[7 empty] | completion is considered to be a declaration of honour by manufacturer | available in the technical file: see list of proofs of conformity (sheet 4) | to be filled in by the manufacturer where required (yellow background) or preferred
1 | Technical characteristics
1.1 | General data
| Synchronization contact | Number | 1 |  | X | declaration
| Synchronization pulse | Duration | As long as synchronization conditions are fulfilled |  | X | declaration
| Local display |  | Phase difference |  | X | declaration
|  |  | Activation of synchronization pulse |  | X | declaration
|  |  | UGEN too high |  | X | declaration
|  |  | UGEN too low |  | X | declaration
| Frequeny range |  | 45 to 55 Hz |  | X | declaration |  |  | (give information on full range)
| Power supply | If applicable | At least one of following voltages: 24 Vdc, 48 Vdc, 110 Vdc or 230 Vac |  | X | declaration |  |  | (give information)
1.2 | Requirements for measuring relays and protection equipment
| Common requirements |  | IEC 60255-1 Normal environmental conditions |  | X | certificate
| Vibration, shock, bump and seismic requirements |  | IEC 60255-21 Environment class 1 |  | X | certificate
| Electromagnetic compatibility requirements |  | IEC 60255-26 Environmental level = zone A |  | X | certificate
| Electromagnetic compatibility requirements |  | IEC 60255-26 Environmental level = zone B |  | X | certificate
| Product safety requirements |  | IEC 60255-27 Rated impulse test voltage = 5 kV peak |  | X | certificate
| Language | Markings, documentation, software, … | min. English |  | X | declaration
2 | Protection functions
2.1 | Voltage monitoring
| Voltage inputs | Rating | 110 Vac, 230 Vac or 400 Vac |  | X | declaration |  |  | (give information)
|  | Overload withstand | Permissible continuous voltage ≥ 1.2 Un Thermal overload ≥ 2 Un during 1s |  | X | declaration
|  | Accuracy | 1% |  | X | declaration |  |  | (give information on accuracy)
|  | Consumption | Max. 3 VA at UN |  | X | declaration |  |  | (give information)
2.2 | Synchronization functions
| Precision | DU | £ 2 % of UN |  | X | declaration |  |  | (give information on precision)
|  | Dj | £ 2° |  | X | declaration |  |  | (give information on precision)
|  | Df | £ 0.02 Hz |  | X | declaration |  |  | (give information on precision)
| Setting limits | DU | 0 to 10 % of UN |  | X | declaration |  |  | (give information on setting range)
|  | Dj | 0 to 10° |  | X | declaration |  |  | (give information on setting range)
|  | Dt | 0 to 1 s (step of 0.1 s) |  | X | declaration |  |  | (give information on setting range)
|  | Df | 0 to 0.5 Hz (step of 0.05 Hz) |  | X | declaration |  |  | (give information on setting range)
| Dead-bus | Function | Possibility to disable |  | X | declaration
3 | Additional information
| Connection scheme | Digital example reference for engineering of the synergrid C10/11 wiring scheme | EPLAN Electric P8 or AutoCAD 2020 in digital version with I/O adressing |  | X | file |  |  | (give information)
compliant
non-compliant
non applicable
EXPLANATIONS FOR COMPLETING THE CHECKLIST AND FOR COMPILING THE TECHNICAL FILE
Column | Title | Remarks
B to E | Characteristic & Requirement | According to the requirements in Technical Prescriptions C10/11 ed2.1 (01/09/2019). New developments and thus resulting requirements in de C10/11 prescription (master document and amendments) nothwithstanding they might not yet be reflected in this specification, are applicable.
F | Reference C10/11 | If applicable, the relevant section is provided.
G | Applicable on what type of relay?
H | Required proof of conformity | The following options are possible:
1. A declaration of honour by the manufacturer regarding conformity with the requirement is sufficient. In this case, the filling in of columns L and N in combination with the signing of the conformity declaration in the first tab applies as the declaration of honour of the manufacturer. There is no need for a separate document.
2. A certificate, report or test report is required. In this case, column M needs to be completed with a clear reference to the provided proofs of conformity (sheet 3).
Conditions for a valid proof of conformity: - to be available in Dutch, French, English or German. Other languages are not accepted. - to be available as a separate document in the technical file. Hyperlinks to online documents without the presence of the document itself, or to web pages, are not accepted as valid proof of conformity. - a document with a unique file name (reference), included in the list of proofs of conformity in tab 4, together with an explanation of the content of the document. - additional: conditions for a valid certificate or test report: see tab 1 (declaration of conformity) - Certificates have been drawn up by an EN 45011 (or ISO 17065:2012) certification body accredited for these materials. - Test reports have been drawn up by an ISO 17025:2005 or ISO 17065:2012 laboratory accredited for these tests.
I | C10/11 Compliant? | The filling in of column L is a declaration of honour of the manufacturer concerning the conformity of the units with the relevant requierment.
J | Manufacturer’s reference of proof of conformity | Each piece of evidence used to demonstrate the required conformity shall have a unique reference number, specified in this column. However, the same piece of evidence may be used as evidence for more than one requirement if its contents permit it. Each supporting document mentioned in this column must be completed in sheet 3 "Proofs of conformity" together with an explanation, and must be present as a separate document in the technical file. See tab 4 "Proofs of conformity" for the conditions for a valid proof of conformity.
K | Additional information | Here the manufacturer has room for explanations as requested.
L | Evaluation Synergrid | This column can be filled in by Synergrid during the study of the homologation application.
M | Explanation Synergrid | This column can be filled in by Synergrid during the study of the homologation application.

## Part 2 - Test labo
SPECIFICATION FOR SYNCHROCHECK RELAYS C10/24 (09/12/2026)
2. Checklist according to the requirements in Technical Prescriptions C10/11 ed2.4 (15/10/2025) - part laboratory-checks
|  | (brand name) | (model name)
|  | Characteristic | Requirement | Reference C10/11 | C10/24 Synchronoscope relay | Required proof of conformity | C10/11 Compliant? | Evaluation Synergrid | Explanation Synergrid
completion is considered to be a declaration of honour by the test labo
4 | Laboratory checks
| Sample relay and software | Sample relay to perform tests | Deliver sample relay and software |  | X | declaration
| Preparation of test | Connecting all elements to perform a Synergrid C10/11 scheme | Report the feasibility and coherence with the documentation |  | X | declaration
| U ramping - Visualization | Ugen too low, Sync pulse and Ugen too high indications | Visual check of functional behaviour |  | X | test report
| U ramping | Allowed voltage difference | Sync pulse within set voltage window (functional behaviour) |  | X | test report
| j ramping | Allowed phase difference | Sync pulse within set phase window (functional behaviour) |  | X | test report
| j sync | Allowed phase difference | Sync pulse within set phase window (time measurement) |  | X | test report
| Report of the setting values |  | Note the settings of the relay |  | X | test report
| Evaluation | Evaluation | Give review with remarks and issues you experienced on the use and interface on the relay |  | X | test report
compliant
non-compliant
non applicable
VALIDATIONS PERFORMED BY A TEST LABORATORY APPOINTED BY SYNERGRID AS PART OF THE HOMOLOGATION PROCESS

## Part 3 - Proofs of conformity
SPECIFICATION FOR SYNCHROCHECK RELAYS C10/24 (09/12/2025)
3. Composition of the technical file: list of document references of the proofs of conformity referred to in the checklist.
|  | (brand name) | (model name)
No. | Manufacturer-references of the proofs of conformity according to the references given in column L of the checklist | Description | Evaluation Synergrid