## Read me first
Dear reader,
This exel sheet is a help to list the documents, certificates or reports to deliver in the technical file required by Synergrid specification C4/10-2
As a majority of the requirements of Synergrid specification C4/10-2, are covert by safety and performance standards, delivered certificates or test reports proving the compliance to the required standards (TRF) are prove of compliance.
Conformity required to standard:
NBN EN 61347-1, (safety) (*)
NBN EN 61347-2-13 (safety) (*)
NBN EN 62384 (performance) (*)
IEC 62386 (For the applicable parts 10x, 2xx and 3xx)
For specific requirements of the specification C4/11-3 (example; Corrosion test, Wind- vibration test, …) reports complying to the specific test process must be delivered.
This file is only an information file that will be submitted to the Synergrid homologation workgroup. A luminaire (family) will only be homologated, as it had pass all the homologation process and it is published on the official Synergid list of homologated luminaires

## LBE To Fill in by applicant
Applicant
Manufacturer
Control gear type
Manufacturers type of documents, certificates and reports delivered in technical file (choice list)
|  | For performance, the control gear is compliant to: | [7 empty] | -
|  | For safety, the control gear is compliant to: | [7 empty] | -
|  | Control gear registered in the DiiA database of DALI-2 certified products | [7 empty] | -
|  | Documents to deliver (Specific requirements) | Technical file SubDirectory number | Sample: delivered to Synergrid | Technical dossier: Certificate or equivalent reports of compliance with the standard to deliver by applicant |  |  |  |  | File name of the document | Check by Synergrid | Check by CE4 commission | Comments Laborelec
|  |  |  | To check by Synergrid homologation commission | ENEC: Certificate + Report | Report of conformity to safety standards | ENEC+ : Certificate + Report | Report of conformity to performance standards | Specific test or specific test sample
| General document | Request document for control gear family | 01 | [5 empty] | Specific document/declaration to deliver |  | - | -
| General document | Technical information for the control gear family | 02 | [5 empty] | Specific document/declaration to deliver |  | - | -
| General document | Declaration that LED control gear is registered in the DiiA (Digital Illumination Interface Alliance) database of DALI-2 certified products | 03 | [5 empty] | Specific document/declaration to deliver |  | - | -
| General document | Declaration CE marking | 04 | [5 empty] | Specific document/declaration to deliver |  | - | -
2019 § | 2019 Chapter | 2019 Requirements | Technical file SubDirectory number | Sample: delivered to Synergrid | Technical dossier: Certificate or equivalent reports of compliance with the standard to deliver by applicant |  |  |  |  | Technical File - Type of documents to deliver (Specific requirements) | File name of the document | Check by Synergrid | Check by Laborelec | Comments Laborelec
|  |  |  | To check by Synergrid homologation commission | ENEC: Certificate + Report | Report of conformity to safety standards | ENEC+ : Certificate + Report | Report of conformity to performance standards | Specific test or specific test sample
4 |  | Performance Control gear must meet the specifications of standard EN 62384 | 07 |  | X | X |  |  | - | - |  | - | -
|  | Safety Control gear must meet the specifications of standards EN 61347-1 and EN 61347-2-13 | 06 |  |  |  | X | X | has to cover the 005 range (Led type, amount of LED, LED current,…) | - |  | - | -
7 |  | Lifespan of LED equipment | 08 | [5 empty] | Vibration §15.3 | Signed declaration + Results test reports |  | - | -
8.2.3 |  | Surge protection According to the EN 61000-4-5 | 09 | [8 empty] | -
8.2.4 |  | Electromagnetic compatibility (EMC) | 10 | [8 empty] | -
|  | Emission | [6 empty] | If applicable Wind test § 15.2 |  |  | - | -
|  | - Standard EN 55015 | [6 empty] | X | Specific test reports - Proving control gears are in conformity with the requirements. This report meets the requirements of § 12. and is issued by a laboratory listed in Synergrid document C4/8-A |  | - | -
|  | - Standard EN 61000-3-2 | [6 empty] | X | Specific test reports - Proving control gears are in conformity with the requirements. This report meets the requirements of § 12. and is issued by a laboratory listed in Synergrid document C4/8-A |  | - | -
|  | Immunity | [6 empty] | X |  |  | - | -
|  | IEC/EN 61000-4-2: Electrostatic Discharges | [6 empty] | X | Specific test reports - Proving control gears are in conformity with the requirements. This report meets the requirements of § 12. and is issued by a laboratory listed in Synergrid document C4/8-A |  | - | -
|  | IEC/EN 61000-4-3: Radiated Fields | [6 empty] | X |  |  | - | -
|  | IEC/EN 61000-4-4: Electrical Fast Transients | [5 empty] | X | Test levels higher than standard : specific report needed. If no SPD, has to be done with each driver? |  |  | - | -
|  | IEC/EN 61000-4-5: Surges |  |  |  |  | X | X |  |  |  | - | -
|  | IEC/EN 61000-4-6: Conducted Fields |  |  |  |  | X | X |  |  |  | - | -
|  | IEC/EN 61000-4-8: Magnetic Fields (if applicable) | [6 empty] | / |  |  | - | -
|  | IEC/EN 61000-4-11: Voltage Dips and interruptions |  |  |  |  | X | X |  |  |  | - | -
8.2.5 |  | Inrush Current |  |  |  |  | X | X |  |  |  | - | -
|  | Photometric flicker - According to the method described in CIE TN 006:2016 | 11 |  |  |  | X | X |  | Specific test reports - Proving control gears are in conformity with the requirements. This report meets the requirements of § 12. and is issued by a laboratory listed in Synergrid document C4/8-A |  | - | -
8.2.7 |  | Setpoint current Exceeding the LED setpoint current | [6 empty] | specific report for the luminaire with the highest LED current and highets CCT of the 005 range | Specific test reports - Proving control gears are in conformity with the requirements. This report meets the requirements of § 12. and is issued by a laboratory listed in Synergrid document C4/8-A |  | - | -
9 |  | Energy performance requirements | 12 | [5 empty] | Temperature test report concerning the most critical luminaire (highest LED current, highest # LEDs) |  |  | - | -
9.1 |  | Electrical efficiency | 13 |  |  |  | X | X |  |  |  | - | -
9.4 |  | Current reduction requirements |  |  |  |  | X | X | X | Specific test reports - Proving control gears are in conformity with the requirements. This report meets the requirements of § 12. and is issued by a laboratory listed in Synergrid document C4/8-A |  | - | -
9.3 |  | Current reduction tests |  |  |  |  | X | X |  | Specific test reports - Proving control gears are in conformity with the requirements. This report meets the requirements of § 12. and is issued by a laboratory listed in Synergrid document C4/8-A |  | - | -
10 |  | Protocol for dimming control and communication |  |  |  |  | X | X | X |  |  | - | -
11 |  | Sound Level - NEMA SSL 1-2016 a classification |  |  |  |  | X | X |  | Specific test reports - Proving control gears are in conformity with the requirements. This report meets the requirements of § 12. and is issued by a laboratory listed in Synergrid document C4/8-A |  | - | -
Note on H35: Author: IEC62717 The initial luminous flux of each individual LED module in the measured sample shall not be less than the rated luminous flux by more than 10 %.
Note on H37: Author: IEC62717 For all tested LED modules in a sample, the LED module efficacy shall not be less than 80% of the rated LED module efficacy as declared by the manufacturer or responsible vendor.
Note on H38: Author: IEC62717 See § 9.1
Note on H39: Author: provisions of 9.3 of IEC 62717 apply to the LED luminaire. + For all tested items in the sample, the measured CRI value shall not have decreased by more than: – 3 points from the rated CRI value (see Table 1) for initial CRI values;

## Check requirements C4_10-2
Field with automatic fill in
Fill in Name manufacturer
Fill in luminare type
| Control gear in conformity with specifiactaion C4/10-2 |  |  |  | Content of this sheet is allocated to Synergrid homologation process.
Check-list technical specification CE4/10-2 Control gear (Driver)
Technical file of the control gear |  | Fill in Name manufacturer
Nb § | Requirements | Fill in luminare type
5 | Requirements for control gear
General
Control gear complying to EN 61347-1
| CB report or equivalent | -
| Verification report | -
| ENEC certificate + report | -
| Verification Certificate + report | -
| No report or certificate delivered | -
Control gear complying to EN 61347-2-13
| CB report or equivalent | -
| Verification report | -
| ENEC certificate + report | -
| Verification Certificate + report | -
| No report or certificate delivered | -
Control gear complying to EN 62384
| CB report or equivalent | -
| Verification report | -
| ENEC certificate + report | -
| Verification Certificate + report | -
| No report or certificate delivered | -
4 | Control Gear - General Requirement
| Control gear must be registered in the DiiA (Digital Illumination Interface Alliance) database of DALI-2 certified products | -
| Ambient operating and starting temperature of the LED control gear must be between -20 °C and +50 °C | -
5 | Marking Requirements
5.1 | Marking for LED control gear |  | For information | § 7.1
| Brand, name of manufacturer | - | IEC 61347-1 | a
| Model number or type reference assigned by manufacturer | - | IEC 61347-1 | b
| Rated input voltage range in volts | - | IEC 61347-1 | e
| Rated input current or range in amperes | - | IEC 61347-1 | e
| Power factor | - | IEC 62384
| (Rated) maximum output power or range in Watt | - | IEC 61347-2-13
| Output current range in amperes or milliamperes | - | IEC 61347-2-13
| Output voltage range in volts | - | IEC 61347-2-13
| Indication of connection | - | IEC 61347-1 | k
CE mark and, if applicable, ENEC conformity mark
Serial number, facilitating the traceability of the unit and its period of production, in particular the country of origin, as well as the month and year of production; the conventional meaning of the sign is communicated when the material is delivered
| Designation of point tc and the maximum admissible value | - | IEC 61347-1 | l
| Symbol for thermally protected equipment (if applicable) | - | IEC 61347-1 | m
| IIdentification of the equipotential terminal by the appropriate symbol | - | IEC 61347-1 | f
| Marked in a clear and durable way in accordance with the requirements of § 7.2 of IEC 61347-1 | - | IEC 61347-1 | § 7.2
8 | Constructive and mechanical properties
| Protection against electrical shocks IP2x | -
| Protection against humid and/or dusty environment | -
| Connection terminals must be protected against corrosion and be made from stainless material | -
| Control gear must contain either an appropriate filler or protection intended to guarantee electric isolation | -
Control gear must be furnished with the requisite fasteners necessary for their installation:
| In the space allocated to this purpose In a lighting device itself | -
| In the equipment’s electrical enclosure placed in the lower part of the lamppost or fixed to a vertical or horizontal wall. | -
7 | Requirements for the lifespan
| Lifespan of LED equipment at a failure rate of less than 10% must be at least 100,000 hours when operating at a temperature (tc) of 70 °C | -
Control gear must have withstood endurance tests in accordance with the standard EN 62384
| Cyclical thermal shock test | -
| Supply voltage switching test | -
| Report meets the requirements of § 12. and is issued by a laboratory listed in Synergrid document C4/8-A | -
8 | Electrical requirements
8.1 | Construction requirements
8.1.1 | Electrical connections
Electrical connections occur by means of connection terminals
| Screw terminals | -
| Push terminals | -
| The input connection (230 V) must be compatible with cables having a cross-section between 0.5 mm² and 2.5 mm². | -
| Connection terminals must be equipped with a system that allows easy connection and disconnection without special tools | -
8.1.2 | Internal protection devices
Control gear must:
| Be equipped with a security system that protects it in case of short circuit or open circuit of a LED module. | -
| Incorporate thermal protection that shuts off the LED module in case of overheating of the device. This is in order to prevent all risks of fire | -
8.2 | Electrical characteristics
8.2.1 | Input Voltage
| Performance and requirements included in this technical specification must be guaranteed for the input voltage and frequencies listed in Table 1 | -
8.2.2 | Operation in case of a voltage drop
| When LED control gear shuts down after a input voltage drop (not an interruption in voltage), it must restart automatically without intervention after an input voltage level of 230 VAC is re-established | -
8.2.3 | Surge protection
| Control gear must be surge-resistant | -
| 6 kV between L/N and EQUI | -
| 4 kV between L and N | -
| 2 kV between DALI controls and EQUI | -
| 30 V between DALI/DALI controls | -
| Test is carried out according to the EN 61000-4-5 | -
| Pulses are to be applied as follows: | -
| Five positive pulses (90° phase) | -
| Five negative pulses (270° phase) | -
| Control gear can see its functioning deteriorate during tests (e.g. flickering) but must return to normal mode of operation after completion of the tests without the aid of external intervention. | -
8.2.4 | Electromagnetic compatibility (EMC)
Control gear must meet the following specifications
| Emission | -
| The emission level must meet the requirements of NBN EN 55015 | -
| The radiated emission level must meet the requirements of NBN EN 55015. The test must be performed at minimum dimmed LED current level and at maximum LED current level | -
| The level of current harmonics must meet the requirements of NBN EN 61000-3-2. The test is conducted for power levels of 20% and 100% of the rated power of the LED control gear. | -
Immunity
Following immunity tests are to be carried out according to NBN EN 61547 standard:
| IEC/EN 61000-4-2: Electrostatic Discharges | -
| IEC/EN 61000-4-3: Radiated Fields | -
| IEC/EN 61000-4-4: Electrical Fast Transients | -
| IEC/EN 61000-4-5: Surges | -
| IEC/EN 61000-4-6: Conducted Fields | -
| IEC/EN 61000-4-8: Magnetic Fields (if applicable) | -
| IEC/EN 61000-4-11: Voltage Dips and interruptions | -
| Tests above are conducted for power levels of 20% and 100% of the LED control gear’s rated power in accordance with § 7 of the standard NBN EN 61547 | -
8.2.5 | Inrush current
Following information must be an integral part of the technical dossier submitted
| The peak current in A (Ipeak) | -
| The pulse width in µs at 50% of Ipeak (Twidth) | -
| The method and parameters used in measurement (source impedance, circuit impedance, supply voltage) | -
| Number of devices able to be installed downstream from a circuit breaker | -
| Type C 16A | -
| Type C 25A | -
| Number of devices able to be installed downstream from a fuse | -
| Type gG 16 A | -
| Type gG 20 A | -
| Type gG 25 A | -
| Calculation method enabling the definition of the number of LED drivers following a protection value different than those noted above | -
8.2.6 | Photometric flicker
| Photometric flicker must be measured according to the method described in CIE TN 006:2016 | -
| The percent flicker (also termed “modulation”, expressed as a percentage), may not exceed the “Low Risk level” limit in Figure 18 of the standard IEEE 1789-201 | -
| Tests above are conducted at rated power and at a lower power level of 50% (± 10%) | -
8.2.7 | Exceeding the LED setpoint current
| LED inrush current must remain at all times below 125% of the LED programmed (setpoint) current. | -
| 20% | -
| 50% | -
| 75% | -
| 100% | -
8.2.8 | Conformity
| Conformity to requirements listed in sections hereunder, is evidenced by a test report containing the detailed test conditions and the results obtained. his report meets the requirements of § 12. and is issued by a laboratory listed in Synergrid document C4/8-A. | -
| § 8.2.3. | -
| § 8.2.4. | -
| § 8.2.5. | -
| § 8.2.6. | -
| § 8.2.7 | -
9 | Energy performance requirements
9.1 | Requirements at rated power and input voltage of 230 V
9.1.1 | Electrical efficiency
| The minimum energy efficiency requirements of individual ballasts at full load must comply with the Ecodesign directive (European Union regulation EU2019 / 2020). | -
| Electrical efficiency must be measured according to the standard IEC 62442-3 | -
9.1.2 | Operation in stand-by mode
| When LED control gear with a nominal power of ≤ 100 W is in stand-by mode, the power consumed must be below 1 watt or 1%. | -
| When LED control gear with nominal power of > 100 W is in stand-by mode, the power consumed must be below 1% of the rated input power | -
9.1.3 | Power factor
| Power factor of LED control gear must be greater than or equal to 0.95 when operating at its rated power | -
| Input power, output power and efficiency are measured in accordance with | -
| IEC 62442-3 | -
| Or with a LED module (rated power of the driver) | -
| Test, performed at rated power (without dimming), the equipment is switched on at an different input voltage. After stabilisation, the parameters below are measured: | -
| Input voltage of 207 V | -
| Input current | -
| Input power | -
| Output power | -
| Efficiency of control gear | -
| Power factor | -
| THD | -
| Input voltage of 230 V | -
| Input current | -
| Input power | -
| Output power | -
| Efficiency of control gear | -
| Power factor | -
| THD | -
| Input voltage of 253 V | -
| Input current | -
| Input power | -
| Output power | -
| Efficiency of control gear | -
| Power factor | -
| THD | -
9.1.4 | THD
| The harmonic distortion rate (THD) of LED control gear must be less than or equal to 10% when operating at its rated power and at input voltage of 230 V. | -
9.2 | Current reduction requirements
9.2.1 | Electrical efficiency
| When current is reduced, the electrical efficiency of the LED control gear must remain compliant with the Ecodesign directive (European Union regulation EU2019 / 2020) (see the provisions in § 9.1.1. ): | -
9.2.2 | Power Factor
| When reducing current, the LED control gear's power factor must comply with Table 4 | -
9.2.3 | THD
| When reducing the current, the LED control gear’s harmonic distortion (THD) must comply with Table 5 | -
9.3 | Current reduction tests
For LED equipment, measurements of input power, output power and efficiency are carried out in accordance with
| Standard IEC 62442-3 | -
| Or with a LED module (rated power of the drive) | -
Test, performed at rated power (without dimming), the equipment is switched on at an voltage of 230 V. After stabilisation, the parameters below are measured:
| Input current | -
| Input power | -
| Output power | -
| Efficiency of control gear | -
| Power factor | -
| THD | -
Same parameters are measured after stabilising for dimming values:
| 50% | -
| Input current | -
| Input power | -
| Output power | -
| Efficiency of control gear | -
| Power factor | -
| THD | -
| 35% | -
| Input current | -
| Input power | -
| Output power | -
| Efficiency of control gear | -
| Power factor | -
| THD | -
| 20% | -
| Input current | -
| Input power | -
| Output power | -
| Efficiency of control gear | -
| Power factor | -
| THD | -
9.4 | Conformity
Conformity to requirements listed in sections hereunder, is evidenced by a test report containing the detailed test conditions and the results obtained. his report meets the requirements of § 12. and is issued by a laboratory listed in Synergrid document C4/8-A.
| § 9.1 | -
| § 9.2 | -
| § 9.3 | -
10 | Protocol for dimming control and communication
| Protocol for control and communication DALI 2 is required | -
Current reduction parameters (dimming) must be freely accessible in reading and writing (mode) by means of the interface DALI 2 (without manufacturer intervention).
The driver must be compatible with the 2 different types of dimming:
| Logarithmic (as defined by IEC 62386-102) | -
| Linear (as defined by IEC 62386-207) | -
| It must be possible to switch from one type to the other without intervention by the manufacturer | -
| In case of a DALI 2 communications malfunction, the LED control gear must function as specified by the standard IEC 62386-102, section 9.3 | -
| It must be possible to read the operational information of LED control gear and the LED module. The manufacturer must provide the list of different data storage registers. | -
The following measures/data must be available via the interface DALI 2:
| LED output voltage (V) | -
| LED output current (mA) | -
| Operating state of the driver (ON/OFF/Defective) | -
| Operating state of the LED (ON/OFF/Defective) | -
| Total operating time | -
| Operating time on the different power ranges | -
| Temperature of LED module (°C) | -
| Control gear internal temperature (°C) | -
11 | Sound level
| Only LED control gear classified under “Sound Rating” A and B is authorised. | -
| NEMA SSL 1-2016 : a classification is defined according to the noise level measured at 1 m distance of the LED control gear | -

## Check Certificate + Reports
Control Gear ENEC | Check | Comments
Certificate
ENEC+ certificate number | -
Certification Body | -
Control gear range | - |  | Content of this sheet is allocated to Synergrid homologation process.
Test Report nr | -

## Used lists
SYNERGRID Check-list technical specification CE4/10-2 Drivers
Documents
Choice type …,
Reports
ENEC
-
List options | List options 2
- | -
Reports delivered | Documents delivered
Documents delivered | Documents not delivered
Reports not delivered
Documents not delivered
List options Laborelec
-
In conformity
Not in conformity
Reports missing
Documents missing
Content of this sheet is allocated to Synergrid homologation process.
Legend LBE check
- | -
Pass | Comply to requirements
Pass Family Concept | Comply to requirements based on family concept
Pass Enec | Comply to requirements as ENEC complying
Not applicable | Not applicable
Fail | No information provided
Fail - Missing document | Submitted to CE4 for decision
Fail - No report delivered | Declared in conformity by WG CE4 Homologation. But action applicant required.
?? | No information provided
Submitted to CE4 for decision | Submitted to CE4 for decision
Pass - CE4 Decision | Declared in conformity by WG CE4 Homologation. But action applicant required.
To check by LBE | Check to be done by LBE but luminaire not delivered at moment of update
Check ongoing by LBE | Check by LBE are on going at moment of update
- | -
- | -
- | -
- | -
- | -

## Used list manuf data fillin
1
2
List 1 Manuf answers | 3
- | 4
Yes | 5
No | 6
7
8
For performance, the control gear is compliant to: | 9
- | 10
ENEC (includes automatically ENEC certificate and TRF test report (CB scheme) | 11
EN 62384 | 12
No reports at disposal | 13
14
15
For safety, the control gear is compliant to: | 16
- | 17
ENEC (includes automatically ENEC certificate and TRF test report (CB scheme) | 18
EN 61347-1, EN 61347-2-13 | 19
No reports at disposal | 20
21
22
Used list manuf data | 23
- | 24
ENEC: Certificate and TRF reports proving conformity to standards | 25
TRF test reports proving conformity to safety standards | 26
TRF test reports proving conformity to Performance standards | 27
Specific test reports - Proving control gears are in conformity with the requirements. This report meets the requirements of § 12. and is issued by a laboratory listed in Synergrid document C4/8-A | 28
Comments
-
Content of this sheet is allocated to Synergrid homologation process.