## Read me first
Dear reader,
This exel sheet is a help to list the documents, certificates or reports to deliver in the technical file required by Synergrid specification C4/11-3
As a majority of the requirements of Synergrid specification C4/11-3, are covert by safety and performance standards, delivered certificates or test reports proving the compliance to the required standards (TRF) are prove of compliance.
Conformity required to standard:
IEC 62722-1 and IEC 62722-2-1 or ENEC+
IEC 62717 and IEC 62031 or ENEC+
EN IEC 60598-2-3 or ENEC
EN IEC 60598-2-5 or ENEC
EN IEC 60598-1 or ENEC
For specific requirements of the specification C4/11-3 (example; Corrosion test, Wind- vibration test, …) reports complying to the specific test process must be delivered.
This file is only an information file that will be submitted to the Synergrid homologation workgroup. A luminaire (family) will only be homologated, as it had pass all the homologation process and it is published on the official Synergid list of homologated luminaires
Possibility 1: Luminaire ENEC+ or Compliant to IEC 62722-1 and IEC 62722-2-1 |  | Possibility 2: LED module ENEC+ or Compliant to IEC 62717 and IEC 62031

## LBE To Fill in by applicant
Applicant
Manufacturer
Luminaire type
Manufacturers type of documents, certificates and reports delivered in technical file (choice list)
|  | For performance, the luminaire is compliant to: | [7 empty] | IEC 62722-1 and IEC 62722-2-1
|  | For safety, the luminaire is compliant to: | [7 empty] | - | -
|  | For performance, the LED module is compliant to: | [7 empty] | - | -
|  | For safety, the LED module is compliant to: | [7 empty] | - | -
|  | Is the body of the luminaire made of synthetic material ? | [7 empty] | -
|  | Documents to deliver (Specific requirements) | Technical file SubDirectory number | Sample: delivered to Synergrid | Technical dossier: Certificate or equivalent reports of compliance with the standard to deliver by applicant |  |  |  |  | File name of the document | Check by Synergrid | Check by CE4 commission | Comments
|  |  |  | To check by Synergrid homologation commission | ENEC: Certificate + Report | Report of conformity to safety standards | ENEC+ : Certificate + Report | Report of conformity to performance standards | Specific test or specific test sample
| General document | Request document for luminaire family | 00 | [5 empty] | Specific document/declaration to deliver |  | - | -
| General document | General description of luminaire family | 02 | [5 empty] | Specific document/declaration to deliver |  | - | -
| General document | Information manufacturerr luminaire identification code | 03 | [5 empty] | Specific document/declaration to deliver |  | - | -
| General document | Technical information | 06 | [5 empty] | Specific document/declaration to deliver |  | - | -
| General document | Assembly-maintenance documents | 04 | [5 empty] | Specific document/declaration to deliver |  | - | -
| General document | Mounting instructions documents | 05 | [5 empty] | Specific document/declaration to deliver |  | - | -
| General document | Declaration CE marking | 07 | [5 empty] | Specific document/declaration to deliver |  | - | -
|  | Specific document = Declaration that used synthetic material is in conformity with requirements | 01 | [7 empty] | - | -
| General document | Specific document = Declaration that used materials are in conformity with requirements concerning corrosion (Internal and External parts) | 01 | [5 empty] | Specific document/declaration to deliver |  | - | -
2019 § | 2019 Chapter | 2019 Requirements | Technical file SubDirectory number | Sample: delivered to Synergrid | Technical dossier: Certificate or equivalent reports of compliance with the standard to deliver by applicant |  |  |  |  | Technical File - Type of documents to deliver (Specific requirements) | File name of the document | Check by Synergrid | Check by Laborelec | Comments
|  |  |  | To check by Synergrid homologation commission | ENEC: Certificate + Report | Report of conformity to safety standards | ENEC+ : Certificate + Report | Report of conformity to performance standards | Specific test or specific test sample
5 | General | Performance standard Luminaire IEC 62722-1 & LED Luminaire IEC 62722-2-1 (Or ENEC+) | 08 -09 |  | X | X |  |  | - | Luminaire test reports: TRF proving conformity to performance standards IEC 62722-1 and IEC 62722-2-1 |  | - | -
5 | General | Safety standard Luminaire NBN EN 60598-1 & 60598-2-3 or 60598-2-5 (Or ENEC) | 10 - 11 |  |  |  | X | X | has to cover the 005 range (Led type, amount of LED, LED current,…) | Luminaire test reports: TRF proving conformity to performance standards IEC 62722-1 and IEC 62722-2-1 |  | - | -
5 | General | Performance standard LED Module IEC 62717 (Or ENEC+) | 12 - 13 |  | X | X |  |  | - | Luminaire test reports: TRF proving conformity to performance standards IEC 62722-1 and IEC 62722-2-1 |  | - | -
5 | General | Safety standard LED Module IEC 62031 (Or ENEC) | 14 |  |  |  | X | X | has to cover the 005 range | Luminaire test reports: TRF proving conformity to performance standards IEC 62722-1 and IEC 62722-2-1 |  | - | -
8.3 | Structural and mechanical | Mounting | 20 | [5 empty] | Vibration §15.3 | Specific test report: Vibration test according § 8.5 of C4/11-3 |  | - | -
8.10.1 | Structural and mechanical | Rating that demonstrates the degree of Impact Protection (IK) of the luminaire | 17 |  | X | X |  |  | Tested IK level mentionned in the report | Luminaire test reports: TRF proving conformity to performance standards IEC 62722-1 and IEC 62722-2-1 |  | - | -
8.10.2 |  | Protection against glass breakage | 17 | [6 empty] | Luminaire test reports: TRF proving conformity to performance standards IEC 62722-1 and IEC 62722-2-1 |  | -
8.11 |  | Protection against dust and moisture (IP) | 18 | [6 empty] | Luminaire test reports: TRF proving conformity to performance standards IEC 62722-1 and IEC 62722-2-1 |  | -
8.12 | Structural and mechanical | Resistance to wind load | 21 | [5 empty] | If applicable Wind test § 15.2 | If applicable test report: Wind test according § 8.12 of C4/11-3 on sample "Worst case scenario" |  | - | -
10.9.1 | Electrical | EMC - conducted emission level between 9 kHz and 30 MHz complies with NBN EN 55015 | 19 | [5 empty] | X | Test reports- Luminaires are in conformity with requirements concerning EMC |  | - | -
10.9.1 | Electrical | EMC - radiated emission level between 9 kHz and 30 MHz complies with NBN EN 55015. The test must be performed at minimum and maximum LED current | [6 empty] | X
10.9.1 | Electrical | EMC - radiated emission level between 30 MHz and 300 MHz complies with NBN EN 55015. The test must be performed at minimum and maximum LED current | [6 empty] | X
10.9.1 | Electrical | EMC - current harmonic level complies with NBN EN 61000-3-2. When the LED luminaire is controllable (dimmable), the test must be performed for five dimming levels at equal distance between the minimum and maximum power | [6 empty] | X
10.9.2 | Electrical | EMC - immunity tests according to NBN EN 61547 standard. When the LED luminaire is controllable (dimmable), the above tests shall be performed at the rated LED load for a lighting level dimmed to 50% ± 10% in accordance with § 7 of the NBN EN 61547 standard | [6 empty] | X
10.9.3 | Electrical | EMC - Surge protection test accroding to IEC 61000-4-5 for the following levels: -6 kV between L/N and EQUI -4 kV between L and N; -2 kV between DALI and EQUI controls; -30 V between DALI/DALI controls; Lower levels must be tested. Pulses are to be applied as follows: five positive pulses (90° phase), 5 negative pulses (270° phase). The luminaire may display different functioning during the tests (e.g. flicker), but after the tests should return to normal functioning without external intervention | 19 |  |  |  |  | X | Test levels higher than standard : specific report needed. If no SPD, has to be done with each driver? | Test reports- Luminaires are in conformity with requirements concerning surge prortection The conducted emission level between 9 kHz and 30 MHz must comply with the requirements of the NBN EN 55015 standard; |  | - | -
10.10 | Electrical | Input power of the luminaire may not exceed the power specified by the manufacturer by more than 10%. | 22 |  |  |  | X | X |  | Luminaire test reports: TRF proving conformity to performance standards IEC 62722-1 and IEC 62722-2-1 |  | - | -
11.1 | Photometric | The initial luminous flux of the luminaire may not be less than 90% of the value specified by the manufacturer | 24 |  |  |  | X | X |  | Luminaire test reports: TRF proving conformity to performance standards IEC 62722-1 and IEC 62722-2-1 |  | - | -
11.2 | Photometric | The distribution of the light intensity must be in accordance with the intensity specified by the manufacturer (Annex D of the IEC 62722-1 is use to check the conformity) | [6 empty] | /
11.3 | Photometric | The initial luminous efficacy of the luminaire may not be less than 90% of the value specified by the manufacturer |  |  |  |  | X | X
12.1 | Colorimetric | The measured initial correlated colour temperature of the luminaire may not deviate by more than 10% from the original value specified by the manufacturer |  |  |  |  | X | X
12.2 | Colorimetric | The measured initial colour rendering index of the luminaire must be higher than or equal to the colour rendering index specified by the manufacturer, minus 3 points |  |  |  |  | X | X
13.1 | Photobiological Safety | The luminaire must be classified in Risk Group 0 or 1 (RG0 or RG1) for retinal blue light hazard measured at a distance of 200 mm | 25 | [5 empty] | specific report for the luminaire with the highest LED current and highets CCT of the 005 range | Specific test report for the luminaire with the highest LED current and highest CCT of the proposed range |  | - | -
14.2 | Lifespan | The Lumen Maintenance at 60.000 hours must be higher than or equal to 90% (verified by T° measurement + LM-80 + TM-21) | 15 | [5 empty] | Temperature test report concerning the most critical luminaire (highest LED current, highest # LEDs) | Test reports - LM-80 + TM-21 (Data + calculation) |  | - | -
14.3 | Lifespan | Durability tests according to IEC 62722-2-1 | 09 |  |  |  | X | X |  | Luminaire test reports: TRF proving conformity to performance standards IEC 62722-1 and IEC 62722-2-1 |  | - | -
14.3 | Lifespan | the tq value to be considered is 25°C. | 09 |  |  |  | X | X | X | Luminaire test reports: TRF proving conformity to performance standards IEC 62722-1 and IEC 62722-2-1 |  | - | -
14.4 | Lifespan | The temperature measured at point tc of the LED driver must be lower than or equal to the temperature that corresponds to a life span of 60.000 hours | 11 | [5 empty] | T° test on the most critical luminaire (highest LED current, highest # LEDs) | Luminaire test reports: TRF proving conformity to performance standards IEC 62722-1 and IEC 62722-2-1 |  | - | -
15.4 | Corrosion | Specific Corrosion testreports | [10 empty] | -
15.4.1 | Corrosion | Internal parts | [10 empty] | -
| Corrosion | Salt spray resistance test shall be executed in accordance with the NBN EN ISO 9227 and NBN EN ISO 2143 standards, with the test duration being equal to: | 26 | [5 empty] | X | Specific test report concerning corrosion tests |  | - | -
15.4.2 | Corrosion | External parts | [10 empty] | -
| Corrosion | Externally (visual assessment at 3 m) no surface irregularities such as: ripples, sags, runs, inclusions, porosity, etc. | 26 | [5 empty] | X | Specific test report concerning corrosion tests |  | - | -
| Corrosion | Layer thickness measured in accordance with the NBN EN ISO 2360 standard at 5 points | 26 | [5 empty] | X | Specific test report concerning corrosion tests |  | - | -
| Corrosion | Luminaires with standard coating: environmental conditions category C3 medium risk (NBN EN 12944-2) | [6 empty] | X |  |  | - | -
| Corrosion | Layer thickness measured at 5 different locations (NBN EN ISO 2360) - Average layer thickness at least 60 micrometers - Local layer thickness at least 48 micrometers | 26 | [5 empty] | X | Specific test report concerning corrosion tests |  | - | -
| Corrosion | Luminaires with standard coating: environmental conditions category C4 high risk (NBN EN 12944-2) | [6 empty] | X |  |  | - | -
| Corrosion | Layer thickness measured at 5 different locations (NBN EN ISO 2360) - Average layer thickness at least 100 micrometers - Local layer thickness at least 96 micrometers | 26 | [5 empty] | X | Specific test report concerning corrosion tests | - | - | -
| Corrosion | Minimum adhesion class 2 (not class 0 like Qualicoat) according to the NBN EN ISO 2409 standard (cross cut test) | 26 | [5 empty] | X | Specific test report concerning corrosion tests |  | - | -
| Corrosion | Salt spray corrosion resistance test according to the NBN EN ISO 9227 standard and assessment of the degree of blistering (3 scratch-free plates) according to the NBN EN ISO 4628-2 standard: | 26 | [5 empty] | X | Specific test report concerning corrosion tests |  | - | -
Note on H43: Author: IEC62717 The initial luminous flux of each individual LED module in the measured sample shall not be less than the rated luminous flux by more than 10 %.
Note on H45: Author: IEC62717 For all tested LED modules in a sample, the LED module efficacy shall not be less than 80% of the rated LED module efficacy as declared by the manufacturer or responsible vendor.
Note on H46: Author: IEC62717 See § 9.1
Note on H47: Author: provisions of 9.3 of IEC 62717 apply to the LED luminaire. + For all tested items in the sample, the measured CRI value shall not have decreased by more than: – 3 points from the rated CRI value (see Table 1) for initial CRI values;

## Basic (hidden)
2019 § | 2019 Chapter | 2019 Requirements | Visual | ENEC | Report of conformity to safety standards | ENEC+ | Report of conformity to performance standards | Specific test or specific test sample | Extension LED type | Extension Driver | Extension Familly size (#LEDs, size luminaire) | Equivalence | requirements to transfert from "2015" list to "2019" list | 2015 | 2015 § | 2015 Chapter | 2015 Requirements
5 | General | Safety standard Luminaire NBN EN 60598-1 & 60598-2-3 or 60598-2-5 (Or ENEC) |  | X | X |  |  | - |  |  |  | Y | / | M | 8.1 | Requirements | Safety standard Luminaire NBN EN 60598-1 & 60598-2-3
5 | General | Performance standard Luminaire IEC 62722-1 & LED Luminaire IEC 62722-2-1 (Or ENEC+) |  |  |  | X | X | has to cover the 005 range (Led type, amount of LED, LED current,…) | X |  |  | No ENEC+ in 2015 IEC 62722-2-1 standard available in 2015, but no compliant luminaires --> Not systematicaly received | Ask ENEC+ or report/cert. | M | 8.1 13.1.2 | Requirements | The luminaire must meet the requirements of the standards IEC 62722-2-1 (005 compliance based on Aging test 1000 h @35°C + Switching test 500 as descript in IEC documents) | Content of this sheet is allocated to Synergrid homologation process.
5 | General | Safety standard LED Module IEC 62031 |  | X | X |  |  | - | X |  |  | 2015 : only in the standards list | Ask for report de conformité or cert. ENEC |  | 4.2 | Standards
5 | General | Performance standard LED Module IEC 62717 |  |  |  | X | X | has to cover the 005 range | X |  |  | No ENEC+ in 2015 IEC 62717:2014 standard available in 2015, but no compliant modules --> Not systematicaly received | Ask ENEC+ or report/cert.? |  | 13.1.2 | Luminaire File | report of compliance to standard IEC 62717 (005 compliance based on Aging test 1000 h @35°C + Switching test 500 as descript in IEC documents)
5 | General | Driver in the C4/10-A Synergrid list | [5 empty] | - |  | X |  | Y | / | M | 9 | LED auxiliaries | present on the list “Synergrid C4/10-A auxiliary recognized Synergrid”
5 | General | Working temperature between -20°C et 25°C | [5 empty] | datasheet | X |  |  | 2015 stronger than 2019 | / | M | 8.1 |  | The successful operation for temperatures between -20 ° C and 35 ° C.
5 | General | ta (luminaire) >= 25°C | [5 empty] | datasheet | X |  |  | All 2015 are at least ta=25°C | /
6.1 | Marking | Luminaire's marking compliant with NBN EN IEC 60598-1, NBN EN IEC 60598-2-3 or 60598-2-5 & IEC 62722-2-1 | X | X | X | X | X | - |  |  |  | Y | / | M | 7.1 | Marking | applicable standards for marking apply
6.1 | Marking | LED Module's marking compliant with IEC 62031 et IEC 62717 | X | X | X | X | X | - |  |  |  | Y | / | M | 7.1 | Marking | applicable standards for marking apply
[12 empty] | Removed | / | M | 7.1.1 | Marking | Wiring diagram
6.2 | Marking | Durable, clear, Indelebile, visible during maintenance marking | X |  |  |  |  | - |  |  |  | Y | / | M | 7.1.2 | Marking | Durable, clear, Indelebile, visible during maintenance marking
6.2.1 | Marking | Additionnal Luminaire Marking : CE, identification tracking code, Flux in lumen, LED current in mA, Tc in K and Ra | X |  |  |  |  | - |  |  |  | Y | / | M | 7.1.2 | Marking | Additionnal Luminaire Marking : CE, identification tracking code, Flux in lumen, LED current in mA, Tc in K and Ra, type of optic
6.2.1 | Marking | Additionnal Luminaire Marking : type of optic | X |  |  |  |  | - |  |  |  | Added | Deliver of label with updated markings?
[12 empty] | Removed | / | M | 7.1.2 | Marking | Additionnal Luminaire Marking : type of lighting appliance, Synergrid approval number, dimming control technology
6.2.2 | Marking | Additionnal LED module Marking : Manufacturer's name, identification tracking code, tc position, tp position | X |  |  |  |  | - |  |  |  | Y | / | M | 7.3 | Marking | Additionnal LED module Marking : Manufacturer's name, identification tracking code, tc position, tp position
6.2.2 | Marking | Additionnal LED module Marking : tc value | X |  |  |  |  | - |  |  |  | Added | Deliver of label with updated markings?
7 | Classification | Type 1 | X |  |  |  |  | - |  |  |  | New for type 1: The replacement of the LED module must be possible without the use of tools. | No Type 1 in 2015 list |  | 6 | Classification | Classification
|  | Type 2 | X |  |  |  |  | - |  |  |  | Y | /
|  | Type 3 | X |  |  |  |  | - |  |  |  | Y | /
|  | Type 4 | X |  |  |  |  | - |  |  |  | Y | /
8.1 | Structural and mechanical | Luminaire composition | X |  |  |  |  | - |  |  |  | Y | / |  | 8.2 |  | Composition of the lighting appliance
8.2 | Structural and mechanical | Luminaire body | X |  |  |  |  | - |  |  |  | Y | / |  | 8.2.1 |  | Body of the lighting appliance
8.2 | Structural and mechanical | Luminaire body | [9 empty] | Y |  |  | 8.2.2 |  | Management of the luminaire temperature
8.3 | Structural and mechanical | Mounting | X |  |  |  |  | Vibration §15.3 |  |  |  | Y | / |  | 8.2.3 |  | Fixing
8.4 | Structural and mechanical | Location auxilliary equipement and wiring | X |  |  |  |  | - |  |  |  | Y | / |  | 8.2.4 |  | Space containing the auxiliary equipment and its wiring
8.5 | Structural and mechanical | Optical compartment | X |  |  |  |  | Vibration §15.3 |  |  |  | Y | / |  | 8.2.5 |  | Optical compartment (fitted with an optical system, adjustable if appropriate)
8.6 | Structural and mechanical | Reflector | X |  |  |  |  | - |  |  |  | Y | / |  | 8.2.6 |  | Reflector
8.7.1 | Structural and mechanical | Requirements |  | X | X |  |  | - |  |  |  | Y | / |  | 8.2.7.1 |  | Requirements
8.7.2 | Structural and mechanical | Mounting | X |  |  |  |  | - |  |  |  | Y | / |  | 8.2.7.2 |  | Fixing
8.7.3 | Structural and mechanical | Closing Mechanism | X |  |  |  |  | - |  |  |  | Y | / |  | 8.2.7.3 |  | Closing Mechanism
8.7.4 | Structural and mechanical | Replacement of protective covers | X |  |  |  |  | - |  |  |  | Y | / |  | 8.2.8 |  | Replacement covers
8.8 | Structural and mechanical | Protective sealing joints against dust and water | X |  |  |  |  | - |  |  |  | Y | / |  | 8.2.9 |  | Gasket protecting against dust and water
8.9 | Structural and mechanical | Protection against mechanical stress concentrations | X |  |  |  |  | - |  |  |  | Y | / |  | 8.3 |  | Protection against concentrations of mechanical tensions
8.10.1 | Structural and mechanical | Rating that demonstrates the degree of Impact Protection (IK) of the luminaire |  | (X) | X |  |  | Tested IK level mentionned in the report |  |  |  | Y | / |  | 8.6 |  | Mechanical strength (IK)
8.10.2 | Structural and mechanical | Protection against glass breakage |  | X | X |  |  | - |  |  |  | Y | / |  | 8.6 |  | Mechanical strength (IK)
8.11 | Structural and mechanical | Protection against dust and moisture |  | X | X |  |  | - |  |  |  | Y | / |  | 8.7 |  | Protection against dust and moisture
8.12 | Structural and mechanical | Resistance to wind load | [5 empty] | If applicable Wind test § 15.2 |  |  |  | Y | / |  | 8.8 |  | Wind resistance
8.13 | Structural and mechanical | Resistance to vibrations | [5 empty] | Vibration §15.3 |  |  |  | Y | / |  | 8.9 |  | Resistance to vibrations
8.14 | Structural and mechanical | The weight of the luminaire (including auxiliary equipment) may not exceed 25 kg | X |  |  |  |  | datasheet |  |  |  | Y | / | M | 8.1 | Requirements | max 25kg
8.15 | Structural and mechanical | Ageing and thermal tests |  | X | X |  |  | - |  |  |  | Y | / |  | 8.11 |  | Ageing and heating requirements
8.16 | Structural and mechanical | Resistance to heat, fire and tracking |  | X | X |  |  | - |  |  |  | Y | / |  | 8.12 |  | Resistance to heat, fire and tracking
8.17 | Structural and mechanical | Synthetic materials for the exterior of the luminaire | [5 empty] | Specific document/declaration to deliver |  |  |  | Y |  |  | 12.11.3 |  | Synthetic materials outside the lighting appliance:
9.1 | Corrosion | External parts | [5 empty] | Declaration |  |  |  | Y |  |  | 12.11.1 |  | External parts
9.1.1 | Corrosion | Protection of the body of the luminaire by applying a coating | [5 empty] | Tests reports &15.4.2 |  |  |  | Salt Mist test of 480h in 2015 and 1000h in 2019 | Deliver 1000h test report |  | 8.4.1 8.4.2 |  | Luminaires with normal paint coat Luminaires with double paint coat
[12 empty] | Removed | / |  |  |  | Hardness test Buchholz according to NBN EN ISO 2815,
9.1.2 | Corrosion | Aluminium components without coating | [5 empty] | Qualanod Certificate or declaration |  |  |  | Y |  |  | 8.4.3 |  | Aluminium parts without paint layer
9.1.3 | Corrosion | Protection of the other components | X | [8 empty] | Y |  |  | 8.4.4 |  | Other components
9.2 | Corrosion | Internal parts | [5 empty] | Test reports §15.4.1 |  |  |  | Y |  |  | 12.11.2 |  | Internal parts
10.1 | Electrical | Protection (IP2X) against electric shocks according to NBN EN 60598-1 & 60598-2-3 or 60598-2-5 |  | X | X | [6 empty] | Y | / | M | 8.13.2 | Requirements | Protection (IP2X) against electric shocks
10.2 | Electrical | Insulation resistance and dielectric strength according to NBN EN 60598-1 & 60598-2-3 or 60598-2-5 |  | X | X | [6 empty] | Y | / |  | 8.10 |  | The provisions of the NBN EN 60598-2-3 and NBN EN 60598-1 apply
10.3 | Electrical | Creepage distances and clearances according to NBN EN 60598-1 & 60598-2-3 or 60598-2-5 |  | X | X | [6 empty] | Y | / | M | 8.14 | Requirements | Creepage distances and clearances
10.4 | Electrical | Appropriate wiring to the usual operating voltage and current and shall resist external direct effects | X | X | X | [6 empty] | Y | / | M | 8.16 | Requirements | Wiring shall be appropriate to the usual operating voltage and current and shall resist external direct effects:
10.4 | Electrical | impossible for the wiring to get jammed between moving components | X | [8 empty] | Y | / | M | 8.16 | Requirements | must not be able to be jammed between moving components
10.4 | Electrical | connections using terminal blocks with screw or pressure contacts, or be fitted with safety plugs | X | X | X | [6 empty] | Y | / | M | 8.16 | Requirements | The connections must be made via screw terminals or pressure or fitted with polarizing plugs
10.4 | Electrical | unimpeded and permanent contact under any condition | X | X | X | [6 empty] | Y | / | M | 8.1 | Requirements | The electrical connections must guarantee a definite, permanent electrical contact in all circumstances
10.4 | Electrical | supply cable fixed to the luminaire by means of a tension stop system or a compression gland with incorporated tension stop | X | X | X | [6 empty] | Y | / | M | 8.16 | Requirements | The supply cable shall be fixed to the lighting appliance by a tension stop system or a compression gland with incorporated tension stop
10.5 | Electrical | Temperature of the insulating parts of all the terminal blocks or plugs of the luminaire shall not exceed 100°C. | X | X | X | [6 empty] | Y | / |  | 8.17 |  | the temperature of the insulating parts of all the terminals or terminal blocks in the luminaire shall not exceed 100 °C
10.6 | Electrical | Connection to the power supply by pluggable terminal block OR switch interrupting the supply network when the luminaire is opened. | X | [8 empty] | Y | / |  | 8.17 |  | The connection to the power supply must be effected by means of a pluggable terminal block or a switch interrupting the supply network during the opening of the luminaire
10.6 | Electrical | Connection with an identification of the phase conductors, neutral and ground | X | [8 empty] | Y | / |  | 8.17.1/2 |  | Equipped with an identification of the phase conductors, neutral and ground
10.6 |  | The terminal block’s connection must be designed in such a way that pole reversal due to an incorrect connection is prevented | X | [8 empty] | Y | / |  | 8.17 |  | The terminal connection shall be designed so as to prevent any inversion of the poles following an erroneous connection
[12 empty] | Removed | / |  | 8.17 |  | The terminal contacts shall be made of brass
10.6 | Electrical | Connection designed so that the earthing connection can be made before connecting the live parts and is disconnected last when unplugged | X | [8 empty] | Y | / |  | 8.17.1/2 |  | Designed so that the earthing connection can be made before connecting the live parts and disconnected last when unplugged
10.6 | Electrical | Connection designed for a current of 16 A and voltage of 250 V | X | [8 empty] | Y | / |  | 8.17.1/2 |  | Be designed for Current: 16 A - Voltage: 250V
10.7 | Electrical | Electrical Class I OR II |  | X | X | [6 empty] | Y | / |  | 8.13.1 | Requirements | Electrical Class I OR II
10.7 | Electrical | If Class I, All metal parts are connected permanently and reliably to an earth terminal |  | X | X | [6 empty] | Y | / | M | 8.15 | Requirements | Metal parts of class I luminaires which may become active in the case of an insulation fault power wiring must be connected permanently and reliably to a ground terminal
10.8 | Electrical | Performance and requirements guaranteed for 207-253VAC range (EN 50160 specs) |  | X | X | [6 empty] | Y | / |  | 8.1 | Requirements | proper functioning for a voltage of 230 V network - 50 Hz, according to the NBN EN 50160
10.9.1 | Electrical | EMC - conducted emission level between 9 kHz and 30 MHz complies with NBN EN 55015 |  |  |  |  | X |  |  | X |  | 2015 : only in the standards list | Ask report
10.9.1 | Electrical | EMC - radiated emission level between 9 kHz and 30 MHz complies with NBN EN 55015. The test must be performed at minimum and maximum LED current |  |  |  |  | X |  |  | X |  | 2015 : only in the standards list Check for dimming | Ask report
10.9.1 | Electrical | EMC - radiated emission level between 30 MHz and 300 MHz complies with NBN EN 55015. The test must be performed at minimum and maximum LED current |  |  |  |  | X |  |  | X |  | 2015 : only in the standards list Check for dimming | Ask report
10.9.1 | Electrical | EMC - current harmonic level complies with NBN EN 61000-3-2. When the LED luminaire is controllable (dimmable), the test must be performed for five dimming levels at equal distance between the minimum and maximum power |  |  |  |  | X |  |  | X |  | 2015 : only in the standards list Check for dimming | Ask report
10.9.2 | Electrical | EMC - immunity tests according to NBN EN 61547 standard. When the LED luminaire is controllable (dimmable), the above tests shall be performed at the rated LED load for a lighting level dimmed to 50% ± 10% in accordance with § 7 of the NBN EN 61547 standard |  |  |  |  | X |  |  | X |  | 2015 : only in the standards list Check for dimming | Ask report
10.9.3 | Electrical | EMC - Surge protection test accroding to IEC 61000-4-5 for the following levels: -6 kV between L/N and GND; -4 kV between L and N; -2 kV between DALI and GND controls; -1 kV between DALI/DALI controls; -6 kV between Lineswitch and GND control; -4 kV between Lineswitch and N control. Lower levels must be tested. Pulses are to be applied as follows: five positive pulses (90° phase), 5 negative pulses (270° phase). The luminaire may display different functioning during the tests (e.g. flicker), but after the tests should return to normal functioning without external intervention |  |  |  |  | X | Test levels higher than standard : specific report needed. If no SPD, has to be done with each driver? |  | X |  | 2019 strenger than 2015 | Ask report | M | 10 | Overvoltage | Surge Test 6 kV between L / N and GND and 3 kV between L and N according to EN 61000-4-5;
10.9.3 | Electrical | Use of SPD allowed | X | [8 empty] | Y | / | M | 10 | Overvoltage | To meet these requirements, the luminaire can be equipped with an additional component as protection against surges.
10.10 | Electrical | Input power of the luminaire may not exceed the power specified by the manufacturer by more than 10%. |  |  |  | X | X |  | X |  |  | Y | / |  | 12.17 |  | Measurements “Total system power and harmonics" Synergrid C4/15: La différence entre la puissance maximale reprise dans le dossier technique et celle mesurée doit être comprise entre –10% et +10%
11.1 | Photometric | The initial luminous flux of the luminaire may not be less than 90% of the value specified by the manufacturer |  |  |  | X | X |  | X |  |  | Y | / |  | 8.18.1 |  | must correspond to the value stated by the manufacturer within ± 10 %.
[12 empty] | Removed (in driver) | / |  | 7.1.2 | Marking | Maximum 10% deviation for Power and flux during the dimming (see test 12.18)
11.2 | Photometric | The distribution of the light intensity must be in accordance with the intensity specified by the manufacturer (Annex D of the IEC 62722-1 is use to check the conformity) | [5 empty] | / | X |  |  | 2019 better specified | Contrôle par LBE de X photométries? |  | 8.18.2 |  | The distribution of light intensity must comply with that stated by the manufacturer
11.3 | Photometric | The initial luminous efficacy of the luminaire may not be less than 90% of the value specified by the manufacturer |  |  |  | X | X |  | X |  |  | Y |  |  | 8.18.1 |  | must correspond to the value stated by the manufacturer within ± 10 %.
[12 empty] | Removed |  |  | 8.18.2.1 |  | Chromaticity requirements at 0h and 6000h
[12 empty] | Removed |  |  | 8.18.4 |  | The values FDF and UFF following CIE 121 must be indicated in the measurement reports
[12 empty] | Removed |  |  | 8.18.5 |  | For all luminaires, Class G must be specified for an inclination of 0 ° in accordance with NBN EN 13201-2
12.1 | Colorimetric | The measured initial correlated colour temperature of the luminaire may not deviate by more than 10% from the original value specified by the manufacturer |  |  |  | X | X |  | X |  |  | Y |  |  | 8.18.2.2 |  | CCT cannot deviate by more than 10% from the initial value
[12 empty] | Removed (never tested) | / |  | 8.18.2.2 |  | CCT after a period of 25 % of the lifetime, with a maximum of 6,000 h, cannot differ more than a of maximum of 10% from the initial value
12.2 | Colorimetric | The measured initial colour rendering index of the luminaire must be higher than or equal to the colour rendering index specified by the manufacturer, minus 3 points |  |  |  | X | X |  | X |  |  | Y |  |  | 8.18.2.3 |  | Ra cannot deviate by more than 3 points from the value stated
[12 empty] | Removed (never tested) | / |  | 8.18.2.3 |  | Ra after a period of 25 % of the lifetime, with a maximum of 6,000 h, must be a maximum of 5 points from the value stated by the manufacturer
13.1 | Photobiological Safety | The luminaire must be classified in Risk Group 0 or 1 (RG0 or RG1) for retinal blue light hazard measured at a distance of 200 mm | [5 empty] | specific report for the luminaire with the highest LED current and highets CCT of the 005 range | X |  |  | Y | / |  | 8.18.3 |  | The luminaire shall be classified according to IEC 62471 standard in Risk Group 0 or 1 (RG0 or RG1) for risk "retinal blue light hazard" measured at a distance of 200 mm
14.2 | Lifespan | The Lumen Maintenance at 60.000 hours must be higher than or equal to 90% (verified by T° measurement + LM-80 + TM-21) | [5 empty] | T° test on the most critical luminaire (highest LED current, highest # LEDs) | X |  |  | 2019 stronger than 2015 | Check measured T° with driver specs |  | 8.19.2 |  | The useful life of the luminaire L80B10 (as defined in IEC 62717) is minimum 60,000 hours
[12 empty] | Removed (never tested) | / |  | 8.19.3 |  | Time to the abrupt failure of the luminaire C10 (as defined in IEC 62717) is minimum 60,000 hours
[12 empty] | Removed (never tested) | / |  | 8.19.1 |  | The luminous flux of the luminaire must be at least 90% of the initial value after a period of 25% of the lifetime, with a maximum of 6000 hours
14.3 | Lifespan | Durability tests according to IEC 62722-2-1 |  |  |  | X | X |  | X |  |  | 2019 strenger than 2015 | Ask ENEC+ or report/cert. IEC 62722? |  | 8.19.4/5 |  | Only switching test and Accelerated lifetime test
14.3 | Lifespan | the tq value to be considered is 25°C. |  |  |  | X | X | X |  |  |  | Y | / | M | 8.11 | Requirements | The value of tq of the luminaire is minimum 25 ° C.
14.4 | Lifespan | The temperature measured at point tc of the LED driver must be lower than or equal to the temperature that corresponds to a life span of 60.000 hours | [5 empty] | T° test on the most critical luminaire (highest LED current, highest # LEDs) |  | X |  | 2015 - tc value doesn’t correspond to 60000h | Check measured T° with driver specs | M | 9 | LED auxiliaries | Temperature measured at point tc marked on the component housing does not exceed the value tc when operated at nominal power, at operating ambient temperature of 25 ° C and at nominal voltage
Note on G78: Author: IEC62717 The initial luminous flux of each individual LED module in the measured sample shall not be less than the rated luminous flux by more than 10 %.
Note on G81: Author: IEC62717 For all tested LED modules in a sample, the LED module efficacy shall not be less than 80% of the rated LED module efficacy as declared by the manufacturer or responsible vendor.
Note on G85: Author: IEC62717 See § 9.1
Note on G87: Author: provisions of 9.3 of IEC 62717 apply to the LED luminaire. + For all tested items in the sample, the measured CRI value shall not have decreased by more than: – 3 points from the rated CRI value (see Table 1) for initial CRI values;

## Check requirements C4_11-3
Field with automatic fill in as it is the conclusion of different points of the checkList or granted by the delivered reports or certificates.
|  | Fill in Name manufacturer | Comments
Fill in luminare type
| Luminaire in conformity with specification C4/11-3 | -
Synergrid classification type luminaire (as declared by Synergrid) |  | Fill in Name manufacturer | Comments
Fill in luminare type
| Luminaire Type 1 Luminaire for which the replacement of the LED module and auxiliaries can be performed on site (= at luminaire mounting height). All the internal wiring must be fitted with removable plugs, protected against mis mating preventing erroneous connection. | - |  | Content of this sheet is allocated to Synergrid homologation process.
| Luminaire Type 2 Luminaires for which the replacement of auxiliary can be performed on site (=at luminaire mounting height). All the internal wiring must be fitted with removable plugs, protected against mis mating preventing erroneous connection. | -
| Luminaire Type 3 Luminaire for which the replacement of LED module and auxiliary requires to remove the luminaire from his support. | -
| Luminaire Type 4 Luminaire that cannot be repaired and that will be permanently replaced in case of failure. | -
Technical file of the luminaire |  | Fill in Name manufacturer | Comments
Nb § | Drivers | Fill in luminare type
| Drivers on Synergrid list | -
Reports: Check-list technical specification CE4/11-3 LED Luminaires
Technical file of the luminaire |  | Fill in Name manufacturer | Comments
Nb § | Requirements | Fill in luminare type
5 | Requirements for LED luminaires
General
Luminaire complying to IEC 62722-2-1
| Certificate ENEC+ delivered | -
| - Certificate in conformity: including submitted luminaire | -
| Report EPRS 003 Delivered | -
| - Report in conformity: including submitted luminaire | -
| CB certificate or equivalent delivered | -
| - Certificate in conformity: including submitted luminaire | -
| TRF Report Delivered | -
| - Report in conformity: including submitted luminaire | -
| No report or certificate delivered | -
LED modules in the luminaires must meet the requirements of:
IEC 62717
| Certificate ENEC+ delivered | -
| - Certificate in conformity: including submitted LED modulle | -
| Report EPRS 001 Delivered | -
| - Report in conformity: including submitted LED modulle | -
| CB certificate or equivalent delivered | -
| - Certificate in conformity: including submitted luminaire | -
| TRF Report Delivered | -
| - Report in conformity: including submitted luminaire | -
| No report or certificate delivered | -
IEC 62031
| Certificate ENEC delivered | -
| - Certificate in conformity: including submitted LED modulle | -
| TRF Report Delivered | -
| - Report in conformity: including submitted LED modulle | -
| CB certificate or equivalent delivered | -
| - Certificate in conformity: including submitted luminaire | -
| TRF Report Delivered | -
| - Report in conformity: including submitted luminaire | -
| No report or certificate delivered | -
Luminaire complying to EN 60 598-1 and EN 60 598-2-3
| Certificate ENEC delivered | -
| - Certificate in conformity: including submitted luminaire | -
| TRF Report Delivered | -
| - Report in conformity: including submitted luminaire | -
| CB certificate or equivalent delivered | -
| - Certificate in conformity: including submitted luminaire | -
| TRF Report Delivered | -
| - Report in conformity: including submitted luminaire | -
| No report or certificate delivered | -
Luminaire complying to EN 60 598-1 and EN 60 598-2-5
| Certificate ENEC delivered | -
| - Certificate in conformity: including submitted luminaire | -
| TRF Report Delivered | -
| - Report in conformity: including submitted luminaire | -
| CB certificate or equivalent delivered | -
| - Certificate in conformity: including submitted luminaire | -
| TRF Report Delivered | -
| - Report in conformity: including submitted luminaire | -
| No report or certificate delivered | -
15 | Measurement methods and specific tests
15.1 | Method for measuring the characteristics of the LED luminaires
15.1.1 | General
Measurements shall be performed according to the specifications
| EN 13032-4 | -
| CIE S 025 | -
| IES LM-79 | -
| Performed at an ambient temperature of 25°C ± 1°C | -
| Input voltage of 230.0 VAC ± 0.2% and frequency of 50 Hz ± 0.2% | -
| Luminaire in normal operating position | -
| Stability conditions specified in EN 13032-4, CIE S 025 or IES LM-79 | -
15.1.2 | Distribution of light intensity
| Correct required C half planes and gamma angles | -
15.1.3 | Colorimetry
| Used method | -
| C plane and gamma angle (C0° G60°, C20°) | -
| Directional distribution, determined by means of a goniocolorimeter or goniospectro-radiometer | -
| Determined by means of an integrating sphere | -
15.2 | Resistance to wind load test
| Wind speed must be achieved after two minutes and must then be maintained for two minutes. Test with wind speed of 150 km/h (41.66 m/s) | -
| Luminaire resist the stresses exerted by a wind at a wind speed of 150 km/h (41.66 m/s) | -
| Under stress conditions the luminaire may not show any breakage or permanent deformation and no movement of the appliance relative to its support may occur | -
| Protective diffuser closure device shall always ensure perfect closure, whatever the vibrations to which the luminaire may be subjected | -
| Drag coefficients specified in the final wind tunnel test report | -
| Conclusion: Luminaire complies to wind test requirements | -
15.3 | Vibration Test Report
| Vibration tests carried out in a specialised laboratory according to Synergrid specification C4/11-3 | -
15.3. 1 | Test 1: Determination of mechanical resonance frequency
| Determines the resonance frequency/frequencies with corresponding quality factors | -
15.3. 2 | Test 2: Test around the mechanical resonance frequency
| Non deterioration occurs | -
| Conclusion: Luminaire complies to vibration test requirements | -
15.4 | Corrosion Test Report
15.4.1 | Internal parts
Salt spray resistance test shall be executed in accordance with the NBN EN ISO 9227 and NBN EN ISO 2143 standards, with the test duration being equal to:
| 100 hours for anodised aluminium reflectors and vacuum metallized reflectors | -
| 480 hours for painted reflectors | -
15.4.2 | External parts
Aluminium elements protected against corrosion by:
| Application of paint | -
| Powder coating | -
| Anodization | -
Visual check
| Externally (visual assessment at 3 m) no surface irregularities such as: ripples, sags, runs, inclusions, porosity, etc. | -
Adhesion
| Minimum adhesion class 2 (not class 0 like Qualicoat) according to the NBN EN ISO 2409 standard (cross cut test) | -
Luminaires for environmental conditions category C3 medium risk (NBN EN 12944-2)
| Layer thickness measured at 5 different locations (NBN EN ISO 2360) - Average layer thickness at least 60 micrometres - Local layer thickness at least 48 micrometres | -
Salt spray corrosion resistance test according to the NBN EN ISO 9227 standard and assessment of the degree of blistering (3 scratch-free plates) according to the NBN EN ISO 4628-2 standard:
| Single coating: 1000 hours | -
| Category C3 Conclusion: | -
Luminaires with standard coating: environmental conditions category C4 high risk (NBN EN 12944-2)
| Layer thickness measured at 5 different locations (NBN EN ISO 2360) - Average layer thickness at least 100 micrometres - Local layer thickness at least 96 micrometres | -
Salt spray corrosion resistance test according to the NBN EN ISO 9227 standard and assessment of the degree of blistering (3 scratch-free plates) according to the NBN EN ISO 4628-2 standard:
| Double coating: 1000 hours | -
| Category C4 Conclusion: | -
Check-list technical specification CE4/11-3 LED Luminaires
Luminaire General Requirement
| Drivers on Synergrid list | -
| Correct operation between -20 °C and 25 °C | -
| Temperature ta of the luminaire must be equal to or higher than 25°C. | -
| Damp and/or dusty environments are not considered to be abnormal operating conditions | -
6 | Marking Requirements
6.1 | Normative requirements
| Markings complying to EN 60 598-1 and EN 60 598-2-3 or EN 60598-2-5 | Fail
Fail
| Markings complying to IEC 62722-2-1 | Fail
| Markings complying to IEC 62717 | Fail
| Markings complying to IEC 62031 | Fail
6.2 | Additional markings
| Additional marking (Durability, Lisibility) | -
6.2.1 | Luminaire
| CE-mark | -
| Manufacturing code | -
| Nominal input current (or range) in Amperes | -
| Luminous flux of the luminaire (in lm) | -
| Input current LED (as delivered) in Amps | -
| Information wiring dimming control system (where applicable) | -
| Correlated colour temperature CCT | -
| Colour rendering index CRI | -
| Type of optics | -
6.2.2 | Led Module
| Name of manufacturer tracked | -
| Identification code that allows the LED module to be tracked | -
| tc value. Marking specific position of tc point on LED module | -
| tp value. If different from tc point, marking specific position of tp point on LED module | -
6.2.3 | Auxiliary equipment - driver
| Markings driver meet specification C4/10-2 | -
7 | Classification of LED luminaires
7.1 | Luminaire type 1
Internal Wiring
| All active internal wiring connected to a component must be equipped with a detachable plug including systems that prevent incorrect connections | -
| Passive and unconnected wiring can be integrated in the active internal wiring and connected to a removable connector or connected to a terminal block connector with spring clamps. | -
| When terminal block connectors are used to connect internal wiring, each clamp must be clearly marked using (standard) consistent codes, regardless of the original luminaire components. The codes must consist of symbols, abbreviations or standard names | -
Auxiliary equipment.
| Auxiliaries on body of the luminaire | -
Auxiliaries on removable mounting plate
| Detachable plate | -
| Easily removable | -
| Easily removable and replaceable, without having to remove the luminaire components | -
| Removable and replaceable without having to remove the e luminaire from its support | -
| Equipped with a detachable terminal block | -
| LED module must not fall when disconnected | -
| Mounting plate and the LED driver may not include sharp part | -
Led module
| Replacement of the LED module possible without the use of tools | -
| Led module on body of the luminaire | -
| Led module on removable mounting plate | -
| Easily accessible and detachable | -
| Easily removable as it is clicked it in place | -
| Equipped with a terminal block | -
| LED module must not fall when disconnected | -
| Conclusion : Luminaire Type 1 | -
7.2 | Luminaire type 2
Internal Wiring
| All active internal wiring connected to a component must be equipped with a detachable plug including systems that prevent incorrect connections | -
| Passive and unconnected wiring can be integrated in the active internal wiring and connected to a removable connector or connected to a terminal block connector with spring clamps. | -
| When terminal block connectors are used to connect internal wiring, each clamp must be clearly marked using (standard) consistent codes, regardless of the original luminaire components. The codes must consist of symbols, abbreviations or standard names | -
| Auxiliaries on body of the luminaire | -
| Auxiliaries on removable mounting plate: | -
| Detachable plate | -
| Easily removable | -
| Easily removable and replaceable, without having to remove the luminaire components | -
| Removable and replaceable without having to remove the e luminaire from its support | -
| Conclusion : Luminaire Type 2 | -
7.3 | Luminaire type 3
| Luminaire for which neither the LED module nor the auxiliary equipment can be replaced. The luminaire is removed and replaced in case of malfunction. No additional requirement applies. | -
| Conclusion : Luminaire Type 3 | -
7.4 | Luminaire type 4
| Luminaires for which neither the LED module nor the LED driver can be replaced. No additional requirement applies. | -
| Conclusion : Luminaire Type 4 | -
8 | Structural and mechanical requirements
8.1 | Luminaire composition
| Mounting on non -combustible surfaces (NBN EN 60598-1) | -
| Synthetic materials must be suitable for use in an outdoor atmosphere (rain, sun ...). | -
| Components of the luminaire may not have sharp cutting edges | -
| Constructed such that the excessive build-up of dirt and bird droppings is prevented | -
8.2 | Luminaire body
| Dirt does not accumulate excessively to guarantee the thermal management. | -
| Constructed without dynamic components | -
8.3 | Mounting
| May not cause damage (e.g. by drilling additional openings) to the lighting column, the jib, the wall support or the luminaire itself | -
| System | -
| Using multiple corrosion -resistant bolts | -
| Bolts made of synthetic material are not used | -
| Using a system with a similar safety guarantee | -
| Mounting element provides at least 3 support areas which ensure the luminaire does not tilt | -
| System not influenced by external loads such as wind, vibrations caused by traffic and standard maintenance work | -
| Luminaire replacement possible | -
| Mounting element In accordance with TS C4/12: External diameter d = 60 mm Length l = 100 mm | -
| If an adapter piece is used, then all required tests shall be carried out using this adapter (wind tunnel test, vibration test, corrosion protection, IP and IK tests, etc, | -
| If the insertion depth in the luminaire amounts to less than 100 mm then the contracting authority may request the supply of a decorative ring in the same colour as the luminaire | -
| If gas thread then in accordance with C4/12 | -
| Verification done by "vibrations test" | -
8.4 | Location of auxiliary equipment and wiring
| Appropriate dimensions | -
| Replacement by equivalent components possible | -
| Space directly accessible without the use of non-standard tools | -
8.5 | Optical compartment
| LED lighting sources, lenses and reflectors are built -in in an optical compartment closed off by a diffuser (light cover) or protective glass | -
| The use of liquid thermal paste to improve the cooling process is not acceptable. | -
| Light source correctly placed | -
| The light source shall not become detached from its support due to vibration (see vibration test) | -
| If the light source or the mirror are adjustable then they shall be lockable in any position (no loss of adjustment due to vibration). | -
| Marks for optical adjustment | -
8.6 | Reflector
| Deformation impossible | -
| Securely installed, verification done by "vibrations test" | -
8.7 | Protective cover, diffuser and lenses
8.7.1 | Requirements
| Thermoplastic materials, durability test | -
| The exterior of the bowl and/or lenses shall be designed to prevent potential contamination | -
| Cover can be opened and closed without special tools | -
| If a refractor and/or lenses are used then their correct position shall be ensured | -
8.7.2 | Mounting
| Maximum 8 closing points | -
| Captive components | -
| Cover and bowl can be opened with single standard tool | -
| Protective cover and diffuser are secured to the body | -
| Covers are be replaceable | -
| Connecting parts cannot be in contact with live parts | -
| Connecting parts made of a synthetic material | -
| The material does not show signs of ageing; | -
| Can resist the high temperature of the LED driver or light source if these accidentally come into contact. | -
| Covers provide support for LED drivers and or LED lighting sources. | -
8.7.3 | Closing mechanism
| Developed for repeated use | -
| Synthetic material are excluded | -
| Mounting elements of clips and hinges may be made of synthetic material insofar as these form part of the body, the diffuser and/or the protective cover itself/themselves | -
| Protective cover and diffuser can be easily and accurately placed on the body when closed | -
8.7.4 | Replacement of protective covers
| It is possible to replace a damaged cover without using non standard tools and without the need for full disassembly of the luminaire. | -
8.8 | Sealing
| Quality ensured over time | -
| Made from synthetic material | -
| Resistant against ageing | -
| Resistant against thermal influences | -
| Resistant against external influences | -
| Natural rubber and non-synthetic felt shall not be used | -
| Construction: | -
| Protects against degradation due to maintenance work on the luminaire | -
| The original positioning must be assured at all times | -
| No degradation of any kind is acceptable, regardless of the actions performed o n the luminaire | -
8.9 | Protection against mechanic stress concentrations
| Protection against stress concentrations or notch effects | -
8.10 | Mechanical protection - IK testing
8.10.1 | Mechanical impact (IK) of the luminaire EN 62262
Impact protection according to NBN EN 62262
| Luminaire minimum IK08 | Fail
| Glass light covers minimum IK06 | Fail
8.10.2 | Protection against glass breakage EN 60598-2-3 - EN 60598-2-5
| Glass that fractures into small pieces | -
| Glass having a high impact shock resistance | -
8.11 | Protection against dust and moisture
| Degrees of protection (IP) tests are carried out according to EN 60598-1 | Fail
| Degree of protection minimum IP65 | Fail
8.12 | Resistance to wind loading
| Only for luminaire, with the exception of the light cover, includes external synthetic material | -
| Wind tests are carried out in a wind tunnel as descript in specification C4/11-3 | -
| Resist the stresses exerted by a wind at a wind speed of 150 km/h (41.66 m/s) | -
| Drag coefficients specified | -
8.13 | Resistance to vibrations
| Vibration tests carried out in a specialised laboratory according to Synergrid specification C4/11-3 | -
8.14 | Weight of the luminaire
| Weight may not exceed 25 kg | -
8.15 | Ageing and thermal tests
Meets the requirements of
| EN 60598-1 | Fail
| The temperature of the unprotected parts accessible parts of the luminaire may not exceed 80 ° C for glass and 65 ° C for metal. | -
8.16 | Resistance to heat, fire and leakage currents
| The requirements of EN 60598-1 and EN 60598-2-3 or EN 60598-2-5 must be fulfilled. | Fail
8.17 | Synthetic materials for the exterior of the luminaire
| Test report demonstrating that the luminaire has been protected against UV(A) radiation and weathering of luminaire materials | -
9 | Requirements regarding protection against corrosion
9.1 | External parts
| Components of aluminium or metal alloys: composition almost immune to corrosion. | -
Aluminium or metal alloy elements
| Made of a compound material that ensures the parts are practically immune to corrosion | -
Protected against corrosion, either by applying:
| Paint | -
| Power coating | -
| Anodizing | -
| Bolts, screws, nuts, clips and hinges, made of corrosion-resistant metal | -
| Protection against bimetallic galvanic corrosion | -
| Coating is applied on aluminium in accordance with specifications which are equivalent to Qualicoat | -
9.1.1 | Protection of the body of the luminaire by applying a coating
Luminaires with standard coating: environmental conditions category C3 medium risk (NBN EN 12944-2)
| Delivered test reports in conformity with the requirements | -
Luminaires with standard coating: environmental conditions category C4 high risk (NBN EN 12944-2)
| Delivered test reports in conformity with the requirements | -
9.1.2 | Aluminium components without coating
| Aluminium components on the exterior that have no coating must be anodized | -
| Anodizing should take place in accordance with equivalent Qualanod specifications | -
9.1.3 | Protection of the other components
| Clips and hinges shall be made of corrosion-resistant metals. | -
| Bolts, screws and nuts shall be made of passivated stainless steel (NBN EN ISO 2516) resistant to salt environments, to NBN EN ISO 3506-1, -2 and -3 | -
| Closure mechanisms shall be made of a combination of (to prevent contact corrosion or cold welding) of hot-dip galvanised steel and passivated stainless steel (NBN EN ISO 2516) resistant to salt environments in accordance to NBN EN 10088-1 | -
| Plastic components shall be suitable for exterior applications (rain, sun, etc) | -
9.2 | Internal parts
| Luminaire’s internal elements protected against corrosion | -
| Reflector’s adjusting screws can be made of nylon or any other equivalent synthetic material | -
| Where anodization of aluminium in accordance with the Qualanod guideline is concerned, the minimum layer thickness is 5 µm | -
| Luminaire’s internal parts, classified under atmospheric corrosiveness category C2 | -
10 | Electrical requirements
10.1 | Protection against electric shock
| The requirements of EN 60598-1 and EN 60598-2-3 or EN 60598-2-5 must be fulfilled. | Fail
| Minimum protection IP2x against electric shock | -
| Protection IP2X cannot be degraded after opening or removing the protective diffusers that is necessary for ordinary luminaire maintenance. | -
10.2 | Insulation resistance and dielectric strength
| Insulation resistance and dielectric strength carried out according to EN 60598-1 and EN 60598-2-3 or EN 60598-2-5 | Fail
10.3 | Creepage distances and clearances
| The requirements of EN 60598-1 and EN 60598-2-3 must be fulfilled. | Fail
10.4 | Internal wiring of the luminaire
| The requirements of EN 60598-1 and EN 60598-2-3 or EN 60598-2-5 must be fulfilled. | Fail
| Wiring appropriate for operating voltage and current | -
| Should not be able to get caught between moving components | -
| Wiring resistant against direct external influences: specific mechanical and thermal loads, UV radiation. | -
| Connections must be made using terminal blocks with screw or pressure contacts, or be fitted with safety plugs | -
| Electric connections must also guarantee unimpeded and permanent contact under any condition | -
| Supply cable shall be fixed to the luminaire by means of a tension stop system or a compression gland with incorporated tension stop | -
10.5 | Terminal blocks and plugs
| The requirements of EN 60598-1 and EN 60598-2-3 or EN 60598-2-5 must be fulfilled. | Fail
| At ta = 25 °C and under nominal voltage, temperature of the insulating parts of all the terminals or terminal blocks in the luminaire shall not exceed 100 °C. If this is exceeded, the manufacturer shall provide proof of the greater thermal resistance of the materials used. | -
10.6 | Connection to the power supply
Connection to the power supply must be effected by means of a:
| Pluggable terminal block | -
| Switch interrupting the supply network when the luminaire is opened | -
| Terminal block’s connection must be designed in such a way that pol e reversal due to an incorrect connection is prevented. | -
Connection to the network must meet the following specifications:
| Equipped with an identification of the phase conductors, neutral and ground | -
| Designed so that the earthing connection can be made before connecting the live parts and is disconnected last when unplugged | -
| Designed for a current of 16 A and voltage of 250 V | -
10.7 | Electrical classes
| Provisions of the EN 60598-1 | Fail
LED luminaires must belong to
| Electrical Insulation Class I | -
| Electrical Insulation Class II | -
| Metal parts of class I luminaires which may become active in the case of an insulation fault in the power wiring can be connected permanently and reliably to an earth terminal | -
10.8 | Supply voltage
| Minimum 207 Vac | -
| Maximum 253 Vac | -
10.9 | Electromagnetic compatibility (EMC)
10.9.1 | Emissions
| The conducted emission level between 9 kHz and 30 MHz must comply with the requirements of the NBN EN 55015 standard; | -
| The radiated emission level between 9 kHz and 30 MHz must comply with the requirements of the NBN EN 55015 standard. The test must be performed at minimum and maximum LED current; | -
| The radiated emission level between 30 MHz and 300 MHz (alternative method) must comply with the requirements of the NBN EN 55015 standard. The test must be performed at minimum and maximum LED current; | -
| The harmonic power level must comply with the requirements of the NBN EN 61000-3-2 standard. When the LED luminaire is controllable (dimmable), the test must be performed for five dimming levels at equal distance between the minimum and maximum power. | -
10.9.2 | Immunity
Immunity tests carried out in accordance with:
| NBN EN 61547 | -
| IEC / EN 61000–4-2: Electrostatic Discharges | -
| IEC / EN 61000–4-3: Radiated Fields; | -
| IEC / EN 61000–4-4: Electrical Fast Transients; | -
| IEC / EN 61000–4-6: Conducted Fields; | -
| IEC / EN 61000–4-8: Magnetic Fields (if applicable); | -
| IEC / EN 61000–4-11: Voltage Dips and Interruptions | -
Controllable luminaire (dimmable)
| Tests shall be performed at the rated LED load for a lighting level dimmed to 50% ± 10%, in accordance with § 7 of the NBN EN 61547 standard | -
10.9.3 | Surge protection
Surges
| 6 kV between L/N and GND | -
| 4 kV between L and N | -
| 2 kV between DALI and GND controls | -
| 30 V between DALI/DALI controls | -
10.10 | Input power of the luminaire
| Input power must be measured at the supply terminals of the complete luminaire in accordance with the conditions §15.1 | -
| The input power may not exceed the power specified by the manufacturer by more than 10% | -
11 | Initial photometric requirements
11.1 | Luminous flux of the luminaire
| The initial luminous flux (lm) and system efficacy (lm/W) measured in a laboratory certified to EN ISO 17025 at an ambient temperature of 25°C ± 1°C shall correspond with the values specified by the manufacturer with a tolerance of 10 %. | -
11.2 | Distribution of light intensity
| The light intensity emitted by the luminaires in different directions is measured in a photogoniometer by a laboratory accredited EN ISO 17025 for the field of application. | -
| All photometric data must be reported for the LED luminaire operating at an ambient temperature of 25 ° C ± 1 ° C. | -
| The distribution of the light intensity must be in accordance with the intensity specified by the manufacturer | -
| The comparison method specified in the normative Annex D of the IEC 62722-1 standard shall be used to assess this compliance | -
11.3 | Luminous efficacy of the luminaire
| The initial luminous efficacy of the luminaire may not be less than 90% of the value specified by the manufacturer. | -
12 | Initial colometric requirements
12.1 | Colour temperature (CCT)
| The measured colour temperature of the luminaire at an ambient temperature of 25°C ± 1°C shall deviate by at most 10% from the value specified by the manufacturer. | -
12.3 | Colour rendition (CRI)
| Initial colour rendering index (CRI) must be at least 70 | -
| The permitted deviation between the measured initial colour rendition (0 h) at an ambient temperature of 25°C ± 1°C shall be at most 3 points from the value specified by the manufacturer. | -
13 | Requirement regarding photobiological safety
13.1 | Retinal blue light hazard of the luminaire
| The luminaire must be classified according to IEC 62471 standard in Risk Group 0 or Risk Group1 (RG0 or RG1) for risk measured at a distance 200 mm. | -
| Measurements distance: 200 mm from the light source. | -
13.2 | Transferability of the retinal blue light hazard of the LED module
| LED module is used in various luminaires | -
| Measurement report of the LED module must meet the following requirements: | -
| The measured LED module is clearly identified (LED module identification, LED type, LED colour temperature) | -
| The measurement is performed at a distance of 200 mm from the LED module | -
| The measurement is performed using a LED module without optics | -
| The LED current supplied during the measurement is specified | -
| To ensure the circular field of vision of 11 mrad (refer to the IEC 62471 standard) fully falls within the LED’s illumination surf ace at a distance of 200 mm, the length of the smallest side of the LED’s illumination surface must be larger than 2.2 mm (if the LED’s illumination surface is circular, the surface’s diameter must be larger than 2.2 mm). | -
| Transferability only applies to luminaires: | -
| With a LED current lower than or equal to the value specified in the LED module’s report | -
| With a colour temperature lower than or equal to the value specified in the LED module’s report | -
14 | Lifespan requirements
14.1 | General
14.2 | Luminous flux retention
| The luminous flux retention (Lumen Maintenance) at 60.000 hours must be higher than or equal to 90%, meaning that after 60.000 hours the current of the embedded LEDs must be higher than or equal to 90% of their initial luminous flux. | -
The applicant must provide the following values:
| Time in hours when L90B50 is attained | -
| Time in hours when L90B10 is attained | -
| Luminous flux retention at 100.000 hours (LxxB50= 100 kh) | -
14.3 | Durability tests
Following tests must be performed as permitted by the IEC 62722-2-1
| Either on the LED module (luminaires of type A using LED modules that have been demonstrated to comply with the IEC 62717 standard) | -
| Or on the complete luminaire (luminaires of type B using LED modules that have not been demonstrated to comply with the IEC 62717 standard) | -
14.3.1 | Determining temperature tp or tq
| Temperature at point t p of the LED module must be measured at an ambient temperature of 25°C and at maximum power | -
| Durability tests must be performed for a temperature t p higher than or equal to the temperature measured in the luminaire | -
| When the durability tests are performed on the complete luminaire, the tq value to be considered is 25°C | -
14.3.2 | Temperature cycling test
| Test will be performed in accordance with § 10.3.2 of the IEC 62717 standard | Fail
| Compliance will be verified in accordance with the criteria of the IEC 62717 standard | Fail
14.3.3 | Supply switching test
| The test will be performed in accordance with § 10.3.3 of the IEC 62717 standard. At least 30.000 cycles must be performed. | Fail
| Compliance will be verified in accordance with the criteria of the IEC 62717 standard | Fail
14.3.4 | Accelerated operation life test
| The test will be performed in accordance with § 10.3.4 of the IEC 62717 standard | Fail
| Compliance will be verified in accordance with the criteria of the IEC 62717 standard | Fail
14.4 | Thermal tests of the LED driver
| The temperature at point tc of the LED driver must be measured when it has been normally fitted in the complete luminaire and it functions at an ambient temperature of 25°C, at the rated power (rated LED current) and at the rated voltage. | -
| The temperature measured at point tc of the LED driver must be lower than or equal to the temperature that corresponds to a life span of 60.000 hours as specified by the manufacturer of the LED driver | -

## Extension Old to New C4_11-3
Field with automatic fill in as it is the conclusion of different points of the checkList or granted by the delivered reports or certificates.
|  | Fill in Name manufacturer | Comments
Fill in luminare type
| Luminaire in conformity with specification C4/11-3 | -
Synergrid classification type luminaire (as declared by Synergrid) |  | Fill in Name manufacturer | Comments
Fill in luminare type
| Luminaire Type 1 Luminaire for which the replacement of the LED module and auxiliaries can be performed on site (= at luminaire mounting height). All the internal wiring must be fitted with removable plugs, protected against mis mating preventing erroneous connection. | - |  | Content of this sheet is allocated to Synergrid homologation process.
| Luminaire Type 2 Luminaires for which the replacement of auxiliary can be performed on site (=at luminaire mounting height). All the internal wiring must be fitted with removable plugs, protected against mis mating preventing erroneous connection. | -
| Luminaire Type 3 Luminaire for which the replacement of LED module and auxiliary requires to remove the luminaire from his support. | -
| Luminaire Type 4 Luminaire that cannot be repaired and that will be permanently replaced in case of failure. | -
Technical file of the luminaire |  | Fill in Name manufacturer | Comments
Nb § | Drivers | Fill in luminare type
| Drivers on Synergrid list | -
Reports: Check-list technical specification CE4/11-3 LED Luminaires
Technical file of the luminaire |  | Fill in Name manufacturer | Comments
Nb § | Requirements | Fill in luminare type
5 | Requirements for LED luminaires
General
Luminaire complying to IEC 62722-2-1
| Certificate ENEC+ delivered | -
| - Certificate in conformity: including submitted luminaire | -
| Report EPRS 003 Delivered | -
| - Report in conformity: including submitted luminaire | -
| CB certificate or equivalent delivered | -
| - Certificate in conformity: including submitted luminaire | -
| TRF Report Delivered | -
| - Report in conformity: including submitted luminaire | -
| No report or certificate delivered | -
LED modules in the luminaires must meet the requirements of:
IEC 62717
| Certificate ENEC+ delivered | -
| - Certificate in conformity: including submitted LED modulle | -
| Report EPRS 001 Delivered | -
| - Report in conformity: including submitted LED modulle | -
| CB certificate or equivalent delivered | -
| - Certificate in conformity: including submitted luminaire | -
| TRF Report Delivered | -
| - Report in conformity: including submitted luminaire | -
| No report or certificate delivered | -
IEC 62031
| Certificate ENEC delivered | -
| - Certificate in conformity: including submitted LED modulle | -
| TRF Report Delivered | -
| - Report in conformity: including submitted LED modulle | -
| CB certificate or equivalent delivered | -
| - Certificate in conformity: including submitted luminaire | -
| TRF Report Delivered | -
| - Report in conformity: including submitted luminaire | -
| No report or certificate delivered | -
Luminaire complying to EN 60 598-1 and EN 60 598-2-3
| Certificate ENEC delivered | -
| - Certificate in conformity: including submitted luminaire | -
| TRF Report Delivered | -
| - Report in conformity: including submitted luminaire | -
| CB certificate or equivalent delivered | -
| - Certificate in conformity: including submitted luminaire | -
| TRF Report Delivered | -
| - Report in conformity: including submitted luminaire | -
| No report or certificate delivered | -
Luminaire complying to EN 60 598-1 and EN 60 598-2-5
| Certificate ENEC delivered | -
| - Certificate in conformity: including submitted luminaire | -
| TRF Report Delivered | -
| - Report in conformity: including submitted luminaire | -
| CB certificate or equivalent delivered | -
| - Certificate in conformity: including submitted luminaire | -
| TRF Report Delivered | -
| - Report in conformity: including submitted luminaire | -
| No report or certificate delivered | -
15 | Measurement methods and specific tests
15.1 | Method for measuring the characteristics of the LED luminaires
15.1.1 | General
Measurements shall be performed according to the specifications
| EN 13032-4 | -
| CIE S 025 | -
| IES LM-79 | -
| Performed at an ambient temperature of 25°C ± 1°C | -
| Input voltage of 230.0 VAC ± 0.2% and frequency of 50 Hz ± 0.2% | -
| Luminaire in normal operating position | -
| Stability conditions specified in EN 13032-4, CIE S 025 or IES LM-79 | -
15.1.2 | Distribution of light intensity
| Correct required C half planes and gamma angles | -
15.1.3 | Colorimetry
| Used method | -
| C plane and gamma angle (C0° G60°, C20°) | -
| Directional distribution, determined by means of a goniocolorimeter or goniospectro-radiometer | -
| Determined by means of an integrating sphere | -
15.2 | Resistance to wind load test
| Wind speed must be achieved after two minutes and must then be maintained for two minutes. Test with wind speed of 150 km/h (41.66 m/s) | -
| Luminaire resist the stresses exerted by a wind at a wind speed of 150 km/h (41.66 m/s) | -
| Under stress conditions the luminaire may not show any breakage or permanent deformation and no movement of the appliance relative to its support may occur | -
| Protective diffuser closure device shall always ensure perfect closure, whatever the vibrations to which the luminaire may be subjected | -
| Drag coefficients specified in the final wind tunnel test report | -
| Conclusion: Luminaire complies to wind test requirements | -
15.3 | Vibration Test Report
| Vibration tests carried out in a specialised laboratory according to Synergrid specification C4/11-3 | Pass
15.3. 1 | Test 1: Determination of mechanical resonance frequency
| Determines the resonance frequency/frequencies with corresponding quality factors | Pass
15.3. 2 | Test 2: Test around the mechanical resonance frequency
| Non deterioration occurs | Pass
| Conclusion: Luminaire complies to vibration test requirements | Pass
15.4 | Corrosion Test Report
15.4.1 | Internal parts
Salt spray resistance test shall be executed in accordance with the NBN EN ISO 9227 and NBN EN ISO 2143 standards, with the test duration being equal to:
| 100 hours for anodised aluminium reflectors and vacuum metallized reflectors | -
| 480 hours for painted reflectors | -
15.4.2 | External parts
Aluminium elements protected against corrosion by:
| Application of paint | -
| Powder coating | -
| Anodization | -
Visual check
| Externally (visual assessment at 3 m) no surface irregularities such as: ripples, sags, runs, inclusions, porosity, etc. | -
Adhesion
| Minimum adhesion class 2 (not class 0 like Qualicoat) according to the NBN EN ISO 2409 standard (cross cut test) | -
Luminaires for environmental conditions category C3 medium risk (NBN EN 12944-2)
| Layer thickness measured at 5 different locations (NBN EN ISO 2360) - Average layer thickness at least 60 micrometres - Local layer thickness at least 48 micrometres | -
Salt spray corrosion resistance test according to the NBN EN ISO 9227 standard and assessment of the degree of blistering (3 scratch-free plates) according to the NBN EN ISO 4628-2 standard:
| Single coating: 1000 hours | -
| Category C3 Conclusion: | -
Luminaires with standard coating: environmental conditions category C4 high risk (NBN EN 12944-2)
| Layer thickness measured at 5 different locations (NBN EN ISO 2360) - Average layer thickness at least 100 micrometres - Local layer thickness at least 96 micrometres | -
Salt spray corrosion resistance test according to the NBN EN ISO 9227 standard and assessment of the degree of blistering (3 scratch-free plates) according to the NBN EN ISO 4628-2 standard:
| Double coating: 1000 hours | -
| Category C4 Conclusion: | -
Check-list technical specification CE4/11-3 LED Luminaires
Luminaire General Requirement
| Drivers on Synergrid list | -
| Correct operation between -20 °C and 25 °C | Pass
| Temperature ta of the luminaire must be equal to or higher than 25°C. | -
| Damp and/or dusty environments are not considered to be abnormal operating conditions | Pass
6 | Marking Requirements
6.1 | Normative requirements
| Markings complying to EN 60 598-1 and EN 60 598-2-3 or EN 60598-2-5 | Fail
Fail
| Markings complying to IEC 62722-2-1 | Fail
| Markings complying to IEC 62717 | Fail
| Markings complying to IEC 62384 | Fail
6.2 | Additional markings
| Additional marking (Durability, Lisibility) | -
6.2.1 | Luminaire
| CE-mark | Pass
| Manufacturing code | Pass
| Nominal input current (or range) in Amperes | -
| Luminous flux of the luminaire (in lm) | -
| Input current LED (as delivered) in Amps | -
| Information wiring dimming control system (where applicable) | Pass
| Correlated colour temperature CCT | Pass
| Colour rendering index CRI | Pass
| Type of optics | -
6.2.2 | Led Module
| Name of manufacturer tracked | -
| Identification code that allows the LED module to be tracked | -
| tc value. Marking specific position of tc point on LED module | -
| tp value. If different from tc point, marking specific position of tp point on LED module | -
6.2.3 | Auxiliary equipment - driver
| Markings driver meet specification C4/10-2 | -
7 | Classification of LED luminaires
7.1 | Luminaire type 1
Internal Wiring
| All active internal wiring connected to a component must be equipped with a detachable plug including systems that prevent incorrect connections | -
| Passive and unconnected wiring can be integrated in the active internal wiring and connected to a removable connector or connected to a terminal block connector with spring clamps. | -
| When terminal block connectors are used to connect internal wiring, each clamp must be clearly marked using (standard) consistent codes, regardless of the original luminaire components. The codes must consist of symbols, abbreviations or standard names | -
Auxiliary equipment.
| Auxiliaries on body of the luminaire | -
Auxiliaries on removable mounting plate
| Detachable plate | -
| Easily removable | -
| Easily removable and replaceable, without having to remove the luminaire components | -
| Removable and replaceable without having to remove the e luminaire from its support | -
| Equipped with a detachable terminal block | -
| LED module must not fall when disconnected | -
| Mounting plate and the LED driver may not include sharp part | -
Led module
| Replacement of the LED module possible without the use of tools | -
| Led module on body of the luminaire | -
| Led module on removable mounting plate | -
| Easily accessible and detachable | -
| Easily removable as it is clicked it in place | -
| Equipped with a terminal block | -
| LED module must not fall when disconnected | -
| Conclusion : Luminaire Type 1 | -
7.2 | Luminaire type 2
Internal Wiring
| All active internal wiring connected to a component must be equipped with a detachable plug including systems that prevent incorrect connections | Pass
| Passive and unconnected wiring can be integrated in the active internal wiring and connected to a removable connector or connected to a terminal block connector with spring clamps. | Pass
| When terminal block connectors are used to connect internal wiring, each clamp must be clearly marked using (standard) consistent codes, regardless of the original luminaire components. The codes must consist of symbols, abbreviations or standard names | Pass
| Auxiliaries on body of the luminaire | -
| Auxiliaries on removable mounting plate: | -
| Detachable plate | -
| Easily removable | -
| Easily removable and replaceable, without having to remove the luminaire components | Pass
| Removable and replaceable without having to remove the e luminaire from its support | Pass
| Conclusion : Luminaire Type 2 | -
7.3 | Luminaire type 3
| Luminaire for which neither the LED module nor the auxiliary equipment can be replaced. The luminaire is removed and replaced in case of malfunction. No additional requirement applies. | -
| Conclusion : Luminaire Type 3 | -
7.4 | Luminaire type 4
| Luminaires for which neither the LED module nor the LED driver can be replaced. No additional requirement applies. | -
| Conclusion : Luminaire Type 4 | -
8 | Structural and mechanical requirements
8.1 | Luminaire composition
| Mounting on non -combustible surfaces (NBN EN 60598-1) | Pass
| Synthetic materials must be suitable for use in an outdoor atmosphere (rain, sun ...). | Pass
| Components of the luminaire may not have sharp cutting edges | Pass
| Constructed such that the excessive build-up of dirt and bird droppings is prevented | Pass
8.2 | Luminaire body
| Dirt does not accumulate excessively to guarantee the thermal management. | Pass
| Constructed without dynamic components | Pass
8.3 | Mounting
| May not cause damage (e.g. by drilling additional openings) to the lighting column, the jib, the wall support or the luminaire itself | Pass
| System | -
| Using multiple corrosion -resistant bolts | -
| Bolts made of synthetic material are not used | -
| Using a system with a similar safety guarantee | -
| Mounting element provides at least 3 support areas which ensure the luminaire does not tilt | -
| System not influenced by external loads such as wind, vibrations caused by traffic and standard maintenance work | Pass
| Luminaire replacement possible | Pass
| Mounting element In accordance with TS C4/12: External diameter d = 60 mm Length l = 100 mm | Pass
| If an adapter piece is used, then all required tests shall be carried out using this adapter (wind tunnel test, vibration test, corrosion protection, IP and IK tests, etc, | Pass
| If the insertion depth in the luminaire amounts to less than 100 mm then the contracting authority may request the supply of a decorative ring in the same colour as the luminaire | Pass
| If gas thread then in accordance with C4/12 | -
| Verification done by "vibrations test" | Pass
8.4 | Location of auxiliary equipment and wiring
| Appropriate dimensions | Pass
| Replacement by equivalent components possible | Pass
| Space directly accessible without the use of non-standard tools | Pass
8.5 | Optical compartment
| LED lighting sources, lenses and reflectors are built -in in an optical compartment closed off by a diffuser (light cover) or protective glass | Pass
| The use of liquid thermal paste to improve the cooling process is not acceptable. | Pass
| Light source correctly placed | Pass
| The light source shall not become detached from its support due to vibration (see vibration test) | Pass
| If the light source or the mirror are adjustable then they shall be lockable in any position (no loss of adjustment due to vibration). | -
| Marks for optical adjustment | -
8.6 | Reflector
| Deformation impossible | -
| Securely installed, verification done by "vibrations test" | Pass
8.7 | Protective cover, diffuser and lenses
8.7.1 | Requirements
| Thermoplastic materials, durability test | Pass
| The exterior of the bowl and/or lenses shall be designed to prevent potential contamination | Pass
| Cover can be opened and closed without special tools | Pass
| If a refractor and/or lenses are used then their correct position shall be ensured | Pass
8.7.2 | Mounting
| Maximum 8 closing points | Pass
| Captive components | Pass
| Cover and bowl can be opened with single standard tool | Pass
| Protective cover and diffuser are secured to the body | Pass
| Covers are be replaceable | Pass
| Connecting parts cannot be in contact with live parts | Pass
| Connecting parts made of a synthetic material | Not applicable
| The material does not show signs of ageing; | Not applicable
| Can resist the high temperature of the LED driver or light source if these accidentally come into contact. | Not applicable
| Covers provide support for LED drivers and or LED lighting sources. | -
8.7.3 | Closing mechanism
| Developed for repeated use | Pass
| Synthetic material are excluded | Pass
| Mounting elements of clips and hinges may be made of synthetic material insofar as these form part of the body, the diffuser and/or the protective cover itself/themselves | -
| Protective cover and diffuser can be easily and accurately placed on the body when closed | -
8.7.4 | Replacement of protective covers
| It is possible to replace a damaged cover without using non standard tools and without the need for full disassembly of the luminaire. | Pass
8.8 | Sealing
| Quality ensured over time | Pass
| Made from synthetic material | Pass
| Resistant against ageing | Pass
| Resistant against thermal influences | Pass
| Resistant against external influences | Pass
| Natural rubber and non-synthetic felt shall not be used | Pass
Construction:
| Protects against degradation due to maintenance work on the luminaire | Pass
| The original positioning must be assured at all times | Pass
| No degradation of any kind is acceptable, regardless of the actions performed o n the luminaire | Pass
8.9 | Protection against mechanic stress concentrations
| Protection against stress concentrations or notch effects | Pass
8.10 | Mechanical protection - IK testing
8.10.1 | Mechanical impact (IK) of the luminaire EN 62262
Impact protection according to NBN EN 62262
| Luminaire minimum IK08 | Fail
| Glass light covers minimum IK06 | Fail
8.10.2 | Protection against glass breakage EN 60598-2-3 - EN 60598-2-5
| Glass that fractures into small pieces | -
| Glass having a high impact shock resistance | -
8.11 | Protection against dust and moisture
| Degrees of protection (IP) tests are carried out according to EN 60598-1 | Fail
| Degree of protection minimum IP65 | Fail
8.12 | Resistance to wind loading
| Only for luminaire, with the exception of the light cover, includes external synthetic material | -
| Wind tests are carried out in a wind tunnel as descript in specification C4/11-3 | -
| Resist the stresses exerted by a wind at a wind speed of 150 km/h (41.66 m/s) | -
| Drag coefficients specified | -
8.13 | Resistance to vibrations
| Vibration tests carried out in a specialised laboratory according to Synergrid specification C4/11-3 | Pass
8.14 | Weight of the luminaire
| Weight may not exceed 25 kg | Pass
8.15 | Ageing and thermal tests
Meets the requirements of
| EN 60598-1 | Fail
| The temperature of the unprotected parts accessible parts of the luminaire may not exceed 80 ° C for glass and 65 ° C for metal. | -
8.16 | Resistance to heat, fire and leakage currents
| The requirements of EN 60598-1 and EN 60598-2-3 or EN 60598-2-5 must be fulfilled. | Fail
8.17 | Synthetic materials for the exterior of the luminaire
| Test report demonstrating that the luminaire has been protected against UV(A) radiation and weathering of luminaire materials | Pass
9 | Requirements regarding protection against corrosion
9.1 | External parts
| Components of aluminium or metal alloys: composition almost immune to corrosion. | -
Aluminium or metal alloy elements
| Made of a compound material that ensures the parts are practically immune to corrosion | -
Protected against corrosion, either by applying:
| Paint | -
| Power coating | -
| Anodizing | -
| Bolts, screws, nuts, clips and hinges, made of corrosion-resistant metal | -
| Protection against bimetallic galvanic corrosion | -
| Coating is applied on aluminium in accordance with specifications which are equivalent to Qualicoat | -
9.1.1 | Protection of the body of the luminaire by applying a coating
Luminaires with standard coating: environmental conditions category C3 medium risk (NBN EN 12944-2)
| Delivered test reports in conformity with the requirements | -
Luminaires with standard coating: environmental conditions category C4 high risk (NBN EN 12944-2)
| Delivered test reports in conformity with the requirements | -
9.1.2 | Aluminium components without coating
| Aluminium components on the exterior that have no coating must be anodized | -
| Anodizing should take place in accordance with equivalent Qualanod specifications | -
9.1.3 | Protection of the other components
| Clips and hinges shall be made of corrosion-resistant metals. | -
| Bolts, screws and nuts shall be made of passivated stainless steel (NBN EN ISO 2516) resistant to salt environments, to NBN EN ISO 3506-1, -2 and -3 | -
| Closure mechanisms shall be made of a combination of (to prevent contact corrosion or cold welding) of hot-dip galvanised steel and passivated stainless steel (NBN EN ISO 2516) resistant to salt environments in accordance to NBN EN 10088-1 | -
| Plastic components shall be suitable for exterior applications (rain, sun, etc) | -
9.2 | Internal parts
| Luminaire’s internal elements protected against corrosion | -
| Reflector’s adjusting screws can be made of nylon or any other equivalent synthetic material | -
| Where anodization of aluminium in accordance with the Qualanod guideline is concerned, the minimum layer thickness is 5 µm | -
| Luminaire’s internal parts, classified under atmospheric corrosiveness category C2 | -
10 | Electrical requirements
10.1 | Protection against electric shock
| The requirements of EN 60598-1 and EN 60598-2-3 or EN 60598-2-5 must be fulfilled. | Fail
| Minimum protection IP2x against electric shock | -
| Protection IP2X cannot be degraded after opening or removing the protective diffusers that is necessary for ordinary luminaire maintenance. | -
10.2 | Insulation resistance and dielectric strength
| Insulation resistance and dielectric strength carried out according to EN 60598-1 and EN 60598-2-3 or EN 60598-2-5 | Fail
10.3 | Creepage distances and clearances
| The requirements of EN 60598-1 and EN 60598-2-3 must be fulfilled. | Fail
10.4 | Internal wiring of the luminaire
| The requirements of EN 60598-1 and EN 60598-2-3 or EN 60598-2-5 must be fulfilled. | Fail
| Wiring appropriate for operating voltage and current | -
| Should not be able to get caught between moving components | -
| Wiring resistant against direct external influences: specific mechanical and thermal loads, UV radiation. | -
| Connections must be made using terminal blocks with screw or pressure contacts, or be fitted with safety plugs | -
| Electric connections must also guarantee unimpeded and permanent contact under any condition | -
| Supply cable shall be fixed to the luminaire by means of a tension stop system or a compression gland with incorporated tension stop | -
10.5 | Terminal blocks and plugs
| The requirements of EN 60598-1 and EN 60598-2-3 or EN 60598-2-5 must be fulfilled. | Fail
| At ta = 25 °C and under nominal voltage, temperature of the insulating parts of all the terminals or terminal blocks in the luminaire shall not exceed 100 °C. If this is exceeded, the manufacturer shall provide proof of the greater thermal resistance of the materials used. | -
10.6 | Connection to the power supply
Connection to the power supply must be effected by means of a:
| Pluggable terminal block | -
| Switch interrupting the supply network when the luminaire is opened | -
| Terminal block’s connection must be designed in such a way that pol e reversal due to an incorrect connection is prevented. | Pass
Connection to the network must meet the following specifications:
| Equipped with an identification of the phase conductors, neutral and ground | Pass
| Designed so that the earthing connection can be made before connecting the live parts and is disconnected last when unplugged | Pass
| Designed for a current of 16 A and voltage of 250 V | Pass
10.7 | Electrical classes
| Provisions of the EN 60598-1 | Fail
LED luminaires must belong to
| Electrical Insulation Class I | Pass
| Electrical Insulation Class II | Pass
| Metal parts of class I luminaires which may become active in the case of an insulation fault in the power wiring can be connected permanently and reliably to an earth terminal | Pass
10.8 | Supply voltage
| Minimum 207 Vac | -
| Maximum 253 Vac | -
10.9 | Electromagnetic compatibility (EMC)
10.9.1 | Emissions
| The conducted emission level between 9 kHz and 30 MHz must comply with the requirements of the NBN EN 55015 standard; | -
| The radiated emission level between 9 kHz and 30 MHz must comply with the requirements of the NBN EN 55015 standard. The test must be performed at minimum and maximum LED current; | -
| The radiated emission level between 30 MHz and 300 MHz (alternative method) must comply with the requirements of the NBN EN 55015 standard. The test must be performed at minimum and maximum LED current; | -
| The harmonic power level must comply with the requirements of the NBN EN 61000-3-2 standard. When the LED luminaire is controllable (dimmable), the test must be performed for five dimming levels at equal distance between the minimum and maximum power. | -
10.9.2 | Immunity
Immunity tests carried out in accordance with:
| NBN EN 61547 | -
| IEC / EN 61000–4-2: Electrostatic Discharges | -
| IEC / EN 61000–4-3: Radiated Fields; | -
| IEC / EN 61000–4-4: Electrical Fast Transients; | -
| IEC / EN 61000–4-6: Conducted Fields; | -
| IEC / EN 61000–4-8: Magnetic Fields (if applicable); | -
| IEC / EN 61000–4-11: Voltage Dips and Interruptions | -
Controllable luminaire (dimmable)
| Tests shall be performed at the rated LED load for a lighting level dimmed to 50% ± 10%, in accordance with § 7 of the NBN EN 61547 standard | -
10.9.3 | Surge protection
Surges
| 6 kV between L/N and GND | -
| 4 kV between L and N | -
| 2 kV between DALI and GND controls | -
| 30 V between DALI/DALI controls | -
10.10 | Input power of the luminaire
| Input power must be measured at the supply terminals of the complete luminaire in accordance with the conditions §15.1 | -
| The input power may not exceed the power specified by the manufacturer by more than 10% | -
11 | Initial photometric requirements
11.1 | Luminous flux of the luminaire
| The initial luminous flux (lm) and system efficacy (lm/W) measured in a laboratory certified to EN ISO 17025 at an ambient temperature of 25°C ± 1°C shall correspond with the values specified by the manufacturer with a tolerance of 10 %. | -
11.2 | Distribution of light intensity
| The light intensity emitted by the luminaires in different directions is measured in a photogoniometer by a laboratory accredited EN ISO 17025 for the field of application. | -
| All photometric data must be reported for the LED luminaire operating at an ambient temperature of 25 ° C ± 1 ° C. | -
| The distribution of the light intensity must be in accordance with the intensity specified by the manufacturer | -
| The comparison method specified in the normative Annex D of the IEC 62722-1 standard shall be used to assess this compliance | -
11.3 | Luminous efficacy of the luminaire
| The initial luminous efficacy of the luminaire may not be less than 90% of the value specified by the manufacturer. | -
12 | Initial colometric requirements
12.1 | Colour temperature (CCT)
| The measured colour temperature of the luminaire at an ambient temperature of 25°C ± 1°C shall deviate by at most 10% from the value specified by the manufacturer. | -
12.3 | Colour rendition (CRI)
| Initial colour rendering index (CRI) must be at least 70 | -
| The permitted deviation between the measured initial colour rendition (0 h) at an ambient temperature of 25°C ± 1°C shall be at most 3 points from the value specified by the manufacturer. | -
13 | Requirement regarding photobiological safety
13.1 | Retinal blue light hazard of the luminaire
| The luminaire must be classified according to IEC 62471 standard in Risk Group 0 or Risk Group1 (RG0 or RG1) for risk measured at a distance 200 mm. | -
| Measurements distance: 200 mm from the light source. | -
13.2 | Transferability of the retinal blue light hazard of the LED module
| LED module is used in various luminaires | -
| Measurement report of the LED module must meet the following requirements: | -
| The measured LED module is clearly identified (LED module identification, LED type, LED colour temperature) | -
| The measurement is performed at a distance of 200 mm from the LED module | -
| The measurement is performed using a LED module without optics | -
| The LED current supplied during the measurement is specified | -
| To ensure the circular field of vision of 11 mrad (refer to the IEC 62471 standard) fully falls within the LED’s illumination surf ace at a distance of 200 mm, the length of the smallest side of the LED’s illumination surface must be larger than 2.2 mm (if the LED’s illumination surface is circular, the surface’s diameter must be larger than 2.2 mm). | -
| Transferability only applies to luminaires: | -
| With a LED current lower than or equal to the value specified in the LED module’s report | -
| With a colour temperature lower than or equal to the value specified in the LED module’s report | -
14 | Lifespan requirements
14.1 | General
14.2 | Luminous flux retention
| The luminous flux retention (Lumen Maintenance) at 60.000 hours must be higher than or equal to 90%, meaning that after 60.000 hours the current of the embedded LEDs must be higher than or equal to 90% of their initial luminous flux. | -
The applicant must provide the following values:
| Time in hours when L90B50 is attained | -
| Time in hours when L90B10 is attained | -
| Luminous flux retention at 100.000 hours (LxxB50= 100 kh) | -
14.3 | Durability tests
Following tests must be performed as permitted by the IEC 62722-2-1
| Either on the LED module (luminaires of type A using LED modules that have been demonstrated to comply with the IEC 62717 standard) | -
| Or on the complete luminaire (luminaires of type B using LED modules that have not been demonstrated to comply with the IEC 62717 standard) | -
14.3.1 | Determining temperature tp or tq
| Temperature at point t p of the LED module must be measured at an ambient temperature of 25°C and at maximum power | -
| Durability tests must be performed for a temperature t p higher than or equal to the temperature measured in the luminaire | -
| When the durability tests are performed on the complete luminaire, the tq value to be considered is 25°C | -
14.3.2 | Temperature cycling test
| Test will be performed in accordance with § 10.3.2 of the IEC 62717 standard | Fail
| Compliance will be verified in accordance with the criteria of the IEC 62717 standard | Fail
14.3.3 | Supply switching test
| The test will be performed in accordance with § 10.3.3 of the IEC 62717 standard. At least 30.000 cycles must be performed. | Fail
| Compliance will be verified in accordance with the criteria of the IEC 62717 standard | Fail
14.3.4 | Accelerated operation life test
| The test will be performed in accordance with § 10.3.4 of the IEC 62717 standard | Fail
| Compliance will be verified in accordance with the criteria of the IEC 62717 standard | Fail
14.4 | Thermal tests of the LED driver
| The temperature at point tc of the LED driver must be measured when it has been normally fitted in the complete luminaire and it functions at an ambient temperature of 25°C, at the rated power (rated LED current) and at the rated voltage. | -
| The temperature measured at point tc of the LED driver must be lower than or equal to the temperature that corresponds to a life span of 60.000 hours as specified by the manufacturer of the LED driver | -

## Check Certificate + Reports
Luminaires or LED modules with ENEC+ and ENEC : certification and reports
Luminaire ENEC+ | Check | Comments
Certificate Delivered | -
Report Delivered | -
Check Certificate
ENEC+ certificate number | -
Certification Body | - |  | Content of this sheet is allocated to Synergrid homologation process.
Luminaires range | -
Conclusion | -
Check report
Test Report EPRS 003 nr | -
CCT range type listed in certificate | -
Led module type listed in certificate | -
PCB type listed in certificate | -
Conclusion | -
LED Module ENEC+ | Check | Comments
IEC 62717
Certificate Delivered | -
Report IEC 62717 Delivered | -
Check Certificate
ENEC+ certificate number | -
Certification Body | -
LED module range | -
Conclusion | -
Check report
Test Report EPRS 001 nr | -
CCT range type listed in certificate | -
Led module type listed in certificate | -
PCB type listed in certificate | -
Conclusion | -
LED Module ENEC+ | Check | Comments
IEC 62031
Certificate Delivered | -
Report IEC 62031 Delivered | -
Check Certificate
ENEC certificate number | -
Certification Body | -
LED module range | -
Conclusion | -
Check report
TRF Test Report nr | -
Led module type listed in certificate | -
Conclusion | -
Street Lighting Luminaire ENEC EN IEC 60598-2-3 | Check | Comments
Certificate Delivered | -
Report Delivered | -
Check Certificate
ENEC certificate number | -
Certification Body | -
Luminaires range | -
Conclusion | -
Check report
TRF Test Report | -
Luminaire range type listed in certificate | -
Conclusion | -
Projector Luminaire ENEC EN IEC 60598-2-5 | Check | Comments
Certificate Delivered | -
Report Delivered | -
Check Certificate
ENEC certificate number | -
Certification Body | -
Luminaires range | -
Conclusion | -
Check report
TRF Test Report | -
Luminaire range type listed in certificate | -
Conclusion | -
Luminaires or LED modules with conformity to IEC : CB certification and reports
Luminaire performace - IEC 62722-2-1 | Check | Comments
Certificate Delivered | -
Report Delivered | -
Check Certificate
Certificate number | -
Certification Body | -
Luminaires range | -
Conclusion | -
Check report
Test Report IEC 62722-2-1 | -
CCT range type listed in certificate | -
Led module type listed in certificate | -
PCB type listed in certificate | -
Conclusion | -
LED Module performace - IEC 62717 | Check | Comments
Certificate Delivered | -
Report Delivered | -
Check Certificate
Certificate number | -
Certification Body | -
LED module range | -
Conclusion | -
Check report
Test Report - IEC 62717 | -
CCT range type listed in certificate | -
Led module type listed in certificate | -
PCB type listed in certificate | -
Conclusion | -
LED Module performace - IEC 62031 | Check | Comments
Certificate Delivered | -
Report Delivered | -
Check Certificate
Certificate number | -
Certification Body | -
LED module range | -
Conclusion | -
Check report
Test Report - IEC IEC 62031 | -
CCT range type listed in certificate | -
Led module type listed in certificate | -
Conclusion | -
Street Lighting Luminaire IEC 60 598-2-3 | Check | Comments
Certificate Delivered | -
Report Delivered | -
Check Certificate
IEC 60 598-2-3 certificate number | -
Certification Body | -
Luminaires range | -
Conclusion | -
Check report
TRF Test Report | -
Luminaire range type listed in certificate | -
Conclusion | -
Projector Luminaire IEC 60598-2-5 | Check | Comments
Certificate Delivered | -
Report Delivered | -
Check Certificate
IEC 60 598-2-5 certificate number | -
Certification Body | -
Luminaires range | -
Conclusion | -
Check report
TRF Test Report | -
Luminaire range type listed in certificate | -
Conclusion | -
Test report verification for standarde EN IEC 60598-2-3:2002, AMD1:2011 used in conjunction with IEC 60598-1
Luminaire test verification | Check | Comments
Tests performed :IEC 60598-2-3:2002, AMD1:2011 used in conjunction with IEC 60598-1 | -
General test requirements: all applicable tests executed | -
Light source in conformity with safety standard IEC 62031 | -
Classification of luminaires
Type of electrical protection | -
Luminaire suitable for direct mounting on normally flammable surfaces | -
Luminaire for normal use | -
-
Degree of protection
IP protection minimum IP65 | -
-
Shock protection
Shock protection luminaire minimum IK08 (5J) | -
Shock protection glass cover minimum IK06 (1J) | - |  | IK01 | IK02 | IK03 | IK04 | IK05 | IK06 | IK07 | IK08 | IK09 | IK10
Glass that fractures into small pieces | - |  | 0.14 | 0.2 | 0.35 | 0.5 | 0.7 | 1 | 2 | 5 | 10 | 20
Glass having a high impact shock resistance | -

## Used lists (hidden)
SYNERGRID Check-list technical specification CE4/11-3 LED Luminaires
Documents |  |  | List for Manuf
Choice type …, |  | Type of documents to deliver | Choice type …,
Reports |  | Report of conformity to safety standards | Reports
ENEC |  | ENEC: Certificate + Report | Luminaire ENEC+: luminaire certificate with EPRS 003 report
ENEC+ |  | ENEC+ : Certificate + Report | LED Module ENEC+: LED module certificate with EPRS 001 report
|  | Report of conformity to performance standards | Luminaire ENEC: luminaire certificate with CB scheme TRF report
|  | Specific test or specific test sample | Luminaire CB TRF report
List options | List options 2 |  | Led Module CB TRF report
- | -
Reports delivered | Documents delivered
Documents delivered | Documents not delivered | Data
Reports not delivered |  | Visual inspection on sample by Synergrid
Documents not delivered |  | Specific test report on specific test sample
Test report: Vibration test according § 8.5 of C4/11-3
Test report: Wind test according § 8.12 of C4/11-3 on sample "Worst case scenario"
Specific document = Declaration that used synthetic material is in conformity with requirements
List options Laborelec |  | Specific document = Declaration that used materials are in conformity with requirements concerning corrosion
- |  | Test reports- Luminaires are in conformity with requirements concerning EMC
In conformity |  | Test reports- Luminaires are in conformity with requirements concerning Surge prortection
Not in conformity |  | Specific test report for the luminaire with the highest LED current and highets CCT of the proposed range
Reports missing |  | Temperature test report concerning the most critical luminaire (highest LED current, highest # LEDs)
Documents missing |  | Specific test report concerning corrosion tests
Not delivered
Content of this sheet is allocated to Synergrid homologation process.
Legend LBE check
-
Pass | Comply to requirements
Pass Family Concept | Comply to requirements based on family concept
Pass Enec | Comply to requirements as ENEC complying
Pass Enec+ | Comply to requirements as ENEC+ complying
Not applicable | Not applicable
Fail | No information provided
Fail - Missing document | Submitted to CE4 for decision
Fail - No report delivered | Declared in conformity by WG CE4 Homologation. But action applicant required.
?? | No information provided
Submitted to CE4 for decision | Submitted to CE4 for decision
Pass - CE4 Decision | Declared in conformity by WG CE4 Homologation. But action applicant required.
To check by LBE | Check to be done by LBE but luminaire not delivered at moment of update
Check ongoing by LBE | Check by LBE are on going at moment of update
No performance report delivered | No performance report delivered. Synergrid test report had to be delivered
- | -
- | -
- | -
- | -

## Used list manuf data fillin (hidden)
1
2
List 1 Manuf answers | 3
- | 4
Yes | 5
No | 6
7
8
For performance, the luminaire is compliant to: | 9
- | 10
ENEC+ (includes automatically ENEC certificate and TRF test report (CB scheme) | 11
IEC 62722-1 and IEC 62722-2-1 | 12
No reports at disposal | 13
14
For safety, the luminaire is compliant to: | 15
- | 16
ENEC | 17
IEC EN 60598-2-3 or IEC EN 60598-2-5 / IEC EN 60598-1 | 18
No reports at disposal | 19
20
21
For performance, the module is compliant to: | 22
- | 23
ENEC+ LED module as component of the ENEC+ certificate of the luminaire (Includes automatically ENEC certificate and TRF test report (CB scheme) | 24
ENEC+ only for LED module (Includes automatically ENEC certificate and TRF test report (CB scheme) | 25
IEC 62717 | 26
No reports at disposal | 27
28
For safety, the module is compliant to: | 29
- | 30 |  | Content of this sheet is allocated to Synergrid homologation process.
ENEC | 31
IEC 62031 | 32
33
Used list manuf data | 34
- | 35
ENEC+: Luminaire certificate and EPRS 003 report proving conformity to performance standards IEC 62722-1 and IEC 62722-2-1. This automaticely includes conformity to ENEC safety standarts. Both TRF test reports must be delivered | 36
ENEC+: LED module certificate and EPRS 001 report | 37
ENEC: Luminaire certificate and TRF reports proving conformity to safety standards IEC EN 60598-2-3 or IEC EN 60 598-2-5 and IEC EN 60 598-1 | 38
ENEC: LED module certificate and TRF report (CB scheme) | 39
Specific test report: Vibration test according § 8.5 of C4/11-3 | 40
If applicable test report: Wind test according § 8.12 of C4/11-3 on sample "Worst case scenario" | 41
Specific document = Declaration that used synthetic material is in conformity with requirements | 42
Specific document = Declaration that used materials are in conformity with requirements concerning corrosion | 43
Test reports - Proving luminaires are in conformity with requirements concerning EMC | 44
Test reports - Proving luminaires are in conformity with requirements concerning Surge protection | 45
Specific test report for the luminaire with the highest LED current and highest CCT of the proposed range | 46
Temperature test report concerning the most critical luminaire (highest LED current, highest # LEDs) | 47
Specific test report concerning corrosion tests | 48
Test reports - LM-80 + TM-21 (Data + calculation) | 49
Luminaire test reports: TRF proving conformity to performance standards IEC 62722-1 and IEC 62722-2-1 | 50
Luminaire test reports: TRF proving conformity to safety standards IEC EN 60598-2-3 or IEC EN 60 598-2-5 and IEC EN 60 598-1 | 51
LED Module test reports: TRF proving conformity to performance standards IEC 62717 | 52
LED module test reports: TRF proving conformity to safety standards IEC 62031 | 53
54
55
Comments
If the luminaires is ENEC+ do not fill-in this option
Content of this sheet is allocated to Synergrid homologation process.